CGMPMM-15/2015

TECHNICAL SPECIFICATION 33KV VACUUM CIRCUIT BREAKER WITH CONTROL & RELAY PANELS AND CURRENT TRANSFORMERS

- scope :

This specification covers the manufacture, assembly, supply and delivery at Destination stores of 33 KV (Vacuum) Out Door porcelain clad circuit breakers including current transformers, meters, relays and control panels for outdoor installations. The power system is with neutral solidly earthed. The equipment shall be guaranteed for 5 years.

- APPLICABLE STANDARDS:

Unless otherwise modified in this specification, the Circuit Breakers, Current Transformers etc. shall comply with the following Standards with latest amendments.

IS	13118/1991 – High Voltage A.C. Circuit Breakers.

IEC	62271-100 or latest version – Circuit Breakers.

IS	2705 (Part I to IV/1992) – Current Transformers.

IS	2099/1986 – Bushings for Alternating Voltages.

IS	13010/2003, IS 13779/1999 – Energy Meters.

IS	3231/1986 & 87 – Relays.

IS	1248/2003 – Ammeters & Voltmeters.

IS	13947/(Pt-1993 – Degree of protection provided by Enclosures.

III.	CLIMATIC CONDITIONS:

The climatic conditions under which the equipment shall operate satisfactorily are as indicated at clause No. 22 of General and Financial terms and conditions for supply of materials.

IV.	PRINCIPAL PARAMETERS :

1.	CIRCUIT BREAKERS	                :

1.1.	Nominal System Voltage		: 33KV

1.2	Type		: Vacuum porcelain clad

1.3	Service		:  ---- out door ---

1.4	No. of Poles/Phases		:  ---- THREE ---

1.5	Highest System Voltage		: 36KV

1.6	Rated Frequency		:  ----- 50 Hz ------

1.7	System of earthing		: ---- Neutral solidly grounded ----

1.8	Insulation level		:

1.8.1.	Lightening Impulse withstand Voltage : 170 KV peak

1.8.2   One minute power frequency	:  70 KV (rms)

withstand voltage.

1.8.3	Power frequency withstand	:	          --- 2 KV (rms) ---/1 minute

voltage on Auxiliary circuit

Note : Please note that the above insulation levels supply at the reference conditions of temperate, pressure and humidity specified below :

Temperature :          20 degree C.

Pressure	:	1013 millibars

Humidity	:	11 g/m 3

1.9	Rated Thermal Current	:	1250 A

1.10.	Rated short circuit	:

breaking current

1.10.1.	Symmetrical	:   25 KA

1.10.2.	Asymmetrical	:	   As per IS : 13118/1991 or IEC – 62271-100 or latest version

1.11.	Rating making capacity	:	    2.50 times Rated short circuit breaking Current 				     (Symmetrical)

  - Rated short time withstand

Current for	:     25 KA/3Sec

1.13	Total break time	:      80 m.sec (Max)

1.14	Bushing Insulator

Creepage distance	:	    Not less than 900 mm

1.15.	Mounting	:	--- Steel Structure --- (GI)

1.16.	Rated Operating sequence	:	   --- O-0.3 Sec. – CO– 3 Min – CO.

1.17.	Operating Mechanism	:	Motor operated/ Manual spring Charged. The standard DC Voltage for the operating devices shall be 24V DC. Operating Voltage for motor spring charging mechanism shall be 250V AC single phase. Normally the breaker shall be operated by Power and there shall be provision for manual operation.

1.18.	Terminal Connector	:

1.18.1.	Material	:	--- Aluminium ---

1.18.2.	Suitable for	:	Panther ACSR

1.19.	Limits of temperature	:	The limits of temperature shall be in accordance with.

IS : 13118/IEC- 62271-100 or latest version.

  - Requirement of Simultaneity

of Poles	:	The maximum difference between instants of contact touching during closing and the maximum difference between the instant of contacts separation during opening between 3 poles shall not exceed one half cycle of the rated frequency. The Breaker shall be open and close simultaneously on all three phases for fault on any phase and or all the phases.

1.21	Protection	:	The Breaker shall be provided with

(1) 3 Nos. Over Current (O/C) and

(2) One Earth Fault (1 E/L)  IDMT relays.

3) Anti pumping relay

4) DC Supervision relay

5) Trip Circuit supervision relay

6) Master trip relay (Hand Reset Type)

Note : Over current Relay settings ranging from 50% to 200% in steps of 25% and earth fault relay settings ranging from 20% to 80% in steps of  10%.

“The over current relays shall be Numerical draw out type and all other mechanical relays are of non-draw out type”.

The over current relays should be of reputed make with IDMT characteristics and also with high instantaneous elements for high fault currents and shall comply with IS 3231.

The relays shall have the facility of minimum 4 Nos. fault tripping data such as :

(a) Fault magnitude (b) Date (c) Time (d) Number of trippings

1.22      Auxiliary Power Supply

1.22.1	A.C. Supply	:	250 V + or – 10% (Phase to neutral),

3 phase, 50 HZ + or – 5%,

Effectively earthed system.

1.22.2	D.C. Supply	:	24V + or – 10%, 2 wire ungrounded system.

    - Supply point:

      - :  Auxiliary power supplies listed above will be made

available to each circuit breaker as below :

A.C. Supply	:	Single Feeder

D.C. Supply	:	Single feeder

      - M.C.B. shall be provided at the circuit breaker for each

Incoming A.C. Supply. For D.C. supply double pole

M.C.B. shall be provided. (with different colours for each identification).

2.	CURRENT TRANSFORMERS :	33 KV

2.1	Rated voltage	:	33 KV

2.2.	Type	:	--- Single phase outdoor live tank oil

Cooled Vacuum impregnated type –

2.3.	Earthing	:	--- Solidly earthed ---

  - Insulation level	:

2.4.1.	Nominal system voltage	:	33 KV					.

2.4.2.	Highest system voltage	:	36 KV

2.4.3.	Lighting Impulse withstand voltage : 170 KV

    - One minute power frequency

Withstand voltage

(a)     Primary (HV)	:	70 KV

(b)     Secondary (LV)      :      3 KV

2.5.	Frequency	:	--- 50 Hz ---

2.6.	Transformation ratio	: 400-200-100/1-1-1A

2.7	Rated secondary current (Amp)	:

i)  Core I (Protection)        :	1

ii) Core II (Metering)          :	1

2.8	Rated output (VA):

i)   Protection                     :	15 VA

ii)  Metering                        :	5 VA

2.9      Short time thermal current			25KA/3 Sec

And its duration		:	The short time thermal current should

Suit the breaker rupturing capacity and

Duration to suit the maximum tripping

Time.

2.10.	Accuracy Limit factor		:	--- ≤10 for protective core ---

2.11.	Class of Insulation		:	Immersed in new insulating oil.

2.11.1	Limit of Temp. Rise (Max)		:	55 Degree C

2.12	Rated Continuous Thermal Current:	1250 A

NOTE : The CTs shall be live tank outdoor type and shall be offered with first filling of Oil. The Oil shall conform to the latest IS 335.

technical requirements :

I.	circuit breakers

1.1	design criteria

The equipment will be used in High Voltage system having characteristics as listed in the specification.

The equipment will be installed outdoor in hot, humid and tropical atmosphere.

All equipment, accessories and wiring shall have tropical protection, involving special treatment of metal and insulation against fungus, insects and corrosion.

The maximum temperature in any part of the equipment at specified rating shall not exceed the permissible limits as stipulated in the relevant standards.

The equipment shall be capable of withstanding the dynamic and thermal stresses of listed short circuit current without any damage or deterioration.

The safety clearances of all live parts of the equipment shall be as per relevant standards.

1.2	TYPE AND DUTY:

The circuit breaker shall be outdoor, 3-pole, vacuum type M2 class (minimum 10,000 operations) in case of 11KV having internal isolation without any sequential interlock.

In the event of order, the tenderer have to offer at least one breaker tested in respect of Temperature rise test and Mechanical endurance test of 10,000 Mechanical operations (M2 Class) in presence of purchaser representative as an acceptance test.

The duty of the circuit breaker shall involve satisfactory interruption of short circuit currents as listed in the clause-IV (Principal Parameters).

The breaker shall be capable of interruption of reactive current (lagging/leading) without under/over voltage.

  - CONSTRUCTION FEATURES :

    - GENERAL ARRANGEMENTS :

The circuit breaker shall have fixed type construction consisting three single identical poles, complete with a gang operated mechanism for specified duty. The interrupters shall be enclosed in a sealed porcelain housing conforming to protection to IS:13947 (PT-1) equivalent to IP-65 protection (IS:2147). All three poles of circuit breaker shall be linked together electrically / mechanically to ensure simultaneous closing/tripping of all poles.

The trip free operating mechanism, 3 phase inter connection links shall be completely accommodated in the base. There shall be sufficient clearance between live parts of the circuit breakers and the ground. The circuit breaker shall be complete with operating mechanism, other accessories/materials to ensure complete assembly and proper functioning. The current transformers shall be externally mounted on the supporting structure integrated with circuit Breaker structure. Terminal connectors suitable for Panther ACSR conductor for 33 KV should be supplied for Circuit Breakers and CTs. The circuit breaker shall be provided with proper standard earthing and with terminal earth bar for earthing connection. Suitable interconnection cable from breaker terminal, CTs terminal to control relay panel is 2.5 Sq.mm. PVC copper control cable (un-armored) are to be provided.

Neither the circuit breaker nor any part of the switchgear or its supporting structures shall be permanently strained due to vibration etc. when making or breaking the rated short circuit currents.

The details of any device incorporated in the circuit breakers to limit or control the rate of restriking voltage across the circuit breaking contacts shall be stated.

The vacuum interrupter assembly used in the circuit breakers shall be interchangeable with indigenously available vacuum interrupters (make and type shall be mentioned.).

    - INTERLOCK :

All electrical and mechanical interlocks which are necessary for safe and satisfactory operation of the circuit breaker shall be furnished.

    - AUXILIARY CONTACTS :

Each breaker shall be provided with 4 normally open and 4 normally closed electrically separate spare Auxiliary contacts in addition to those required for its own operation and indication exclusively for purchaser’s use.

The auxiliary contacts shall be convertible type so that normally open contacts can be converted into normally close contacts and vice verse at site.

The auxiliary contacts shall be rated for 10A for AC and 5A for DC.

    - INSULATORS :

Bushing insulators for circuit Breakers shall comply with IS2099-1986 specification for High Voltage porcelain bushings.

Insulators shall be wet process porcelain, brown glazed and free from all blemishes. Ferrous metal parts and hardware shall be hot-dip galvanised.

Insulators shall have adequate mechanical strength and rigidity to withstand the duty 	involved.

When operated at maximum system voltage, there shall be no electrical discharge. Shielding rings, if necessary, shall be provided. Insulation shall be coordinated with basic impulse level of the system. The creepage distance shall correspond to heavily polluted atmosphere.

1.4.	OPERATING MECHANISM:

The operating mechanism shall be motor operated and manual operated for spring closing mechanism with trip free features complete with shut trip coils. All three poles of the breaker shall operate simultaneously. It shall operate in principle in such a way that the closing springs after each closing operation, are automatically charged by the motor and locked in the charged position by a latch. Means shall be provided to charge the springs manually also. Provision shall be made for the slow closing of the VCB without spring charging.

The contact loading spring shall be designed in such a way that the closing stroke be completed and the opening stroke is commenced only from fully closed position. All the breakers shall be suitable for manual operation as well as slow closing without spring charging.

Operation counter and mechanically operated indicator to show whether the circuit breaker is open or closed shall be provided on the circuit breaker operating mechanism.

All manually operating gear shall be so designed that the circuit breaker can be operated by one movement. The mechanism shall be such that the tripping spring can be charged while the circuit breaker is closed and the closing mechanism when charged shall not be operated by vibration caused by the circuit breaker opening under fault conditions. The spring shall be suitable for 4 short reclosing operation.

The mechanism shall be designed for electrical control from remote. Local manual close/trip (lever/button) shall be provided in the mechanism box only.

1.5	CONTROL CUBICLE (MECHANISM BOX)

A common control cubicle shall be furnished to house electricals, controls, monitoring devices and all other accessories except those which must be located on individual poles.

The cubicle shall have protection as per IS-13947 PT-1 equivalent to IP-55 protection (IS-2147) of gasketed whether proof construction, fabricated from sheet steel minimum 2.5mm thick.

The cubicle shall have front access door with lock and keys, and removable gland plate at the bottom for cable entry.

1.6       WIRING & TERMINAL BLOCKS :

1.6.1WIRING

Wiring shall be complete in all respects to ensure proper functioning of the control, protection, monitoring and interlocking schemes.

Wiring shall be done with flexible 650 V grade, PVC insulated switch board wires with 2.5 sq.mm. stranded copper conductor. Wiring between individual poles and control cubicle shall be routed through G.I. Conduits.

Each wire shall be identified at both ends with permanent markers bearing wire numbers as per wiring diagram. The wiring schematic may conform to relevant standards.

Wire termination shall be done with crimping type connectors with insulating sleeves. Wire shall not be spliced between terminals.

All spare contacts of relays, push buttons, auxiliary switchers etc. shall be wired upto terminal blocks in the control cubicle.

1.6.2.	TERMINAL BLOCKS :

Terminal blocks shall be 650 V grade, box clamp type (Nut & Bolt Type).

Not more than two wires shall be connected to any terminal. Spare terminals equal in number to 20% active terminals shall be furnished.

Terminal blocks shall be located to allow easy access. Wiring shall be so arranged that individual wires of an external cable can be connected to constructive terminals.

For CTPT – disconnected type terminal blocks are required.

1.7	NAME/RATING PLATE:

BREAKERS : Each circuit-breaker shall be provided with a name plate or plates legibly and indelibly marked with atleast the following information:

- Name of manufacturer.

- Type of designation and serial number.

- Rated Voltage and current.

- Rated frequency.

- Rated symmetrical breaking capacity.

- Rated making capacity and

- Rated short-time current and its duration.

(which shall be either one or three seconds).

Note :	1.	The word “Rated” need not appear on the name plate, recognised abbreviations may be used to express the above quantities.

2.	When the circuit breaker is fitted with closing and/or tripping devices necessitating any auxiliary supply the nature of the auxiliary supply shall be stated either on the circuit breaker name-plate or in any other acceptable position.

3.	The purchase order No. and date and year of supply and the words TSSPDCL must be etched on the name plate.

CONTROL & RELAY PANELS:

  - CONSTRUCTION :

The Control panels to house meters, relays and other items as specified in clause VI(3) shall be weather proof and vermin proof and of rust-free pressed steel cubicle type with hinged door and locking device. Ventilation louvers shall be provided with GI mech. The frame shall be made of angle iron or structural steel of sufficient weight and strength to ensure alignment. The control panel shall be provided with inter connections, small wiring leads, terminal bolts, fuses, earth bar, multi core cable glands, earth connections etc, The panel should be provided with locking handle with built-in door lock and lock shall be provided with duplicate keys.

The outdoor panels shall be preferable of the following dimensions :-

Height	    1750 mm

Width	     600 mm

Depth	     600 mm

The exterior of the panels shall be painted with dark admiral grey colour and interior should be painted with half white colour. The panel shall be provided with fuse units/MCBs for AC Circuit (both phase and neutral) for all phases of potential Circuit (Potential coil connections to energy meters etc.) DC Control Circuit etc. The internal wiring of the panels shall be with 2.5 sq.mm 650 V grade standard copper PVC Insulated wiring of reputed make.

The Guage of the sheet steel for the front of the panels (where the meters etc. are fixed) and supporting members of the panels shall be of 3 mm thick and for the other members of the panel sheet steel thickness shall be 2 mm.

Wherever control panels are fixed to the breaker structure necessary clearance from the ground to read the meters and to operate the switches shall be maintained. The suitable interconnection cable from breaker terminal, CTs terminal to control relay panel is 2.5 Sq.mm. PVC copper control cable (un-armored) shall be provided.

2.2	PAINTING:

Before painting all non-galvanised parts shall be completely cleaned and made free of rust, scale and grease and all external rough surface cavities on casting shall be filled by metal deposition.   It shall be ensured that Phosphate coating is done by a suitable process on both the external and internal surfaces.  The painting to be done on surface shall be by powder coating process

The interior parts and internal structural steel work shall be cleaned of all scale and rust by sand blasting or other approved method.

All external surface shall receive a minimum of 3 coats of paint. The paint shall be guaranteed for 5 years from the date of receipt of material.

CURRENT TRANSFORMERS :

3.1        CONSTRUCTION

The core shall be high grade non-ageing electrical silicon-laminated steel of low hysterisis loss and high permeability to ensure high accuracy, at both normal and over current.

The secondary terminals shall be brought into a compartment on one side of current transformer for easy access. The Secondary terminal shall be provided with short circuiting arrangements. The secondary taps shall be adequately reinforced to withstand normal handling, without damage.

The current transformers shall be suitable for mounting on steel structures or concrete pedalstals. The necessary flanges, bolts, etc, for the base of the Current Transformer shall be supplied and these shall be galvanised. The current transformer tank and other metal parts shall be galvanised.

The primary of the current transformers shall have double cotton covered roped conductors with insulation by Kraft paper.  The secondary shall be super enameled copper wire.  Details of winding and core including sectional drawings shall be furnished.

The Current Transformers shall be complete in all respects with filling of oil conforming to IS:335 and with oil level indicator with minimum/maximum oil levels.

3.2	NAME/RATING PLATE :

Each Current Transformer shall have the following particulars indelibly marked on it or on a label permanently secure to it or its casing.

- Manufacturer’s Name :

- Manufacturer’s Sl.No. and /or type of designation:

- Rated transformation ratio :

- Rated Frequency

- Highest system voltage

- Insulation level and

- Rated short time thermal current with the associated rate time and rated dynamic current.

The Purchase Order No. and date and year of supply and the words “APTRANSCO” must be etched on the name plate.

VI.	SCHEDULE OF EQUIPMENT

1.	CIRCUIT BREAKERS :

Vacuum Circuit Breaker complete with suitable painted steel support structure (with anchor bolts & nuts) for mounting 1 No. circuit breaker – 3 poles. Mechanism box, control and relay panel and Current Transformers.

Note :	1.	Earth strips as per IS shall be provided for proper earthing of equipments.

2.	Earth bar of copper (suitable for termination of 2 Nos. 40 * 6 mm Flats) shall be provided on Circuit breaker support structure.

3.	Connecting Cable from Breaker to Control panel and Breaker to CTs are to be provided.

3 (i) 	Connecting Cable from Breaker to CTs 6 Core cable of 5 mtrs length from each CT i.e., total 3 x 5 = 15 mtrs / Breaker and from Breaker to Control panel 10 core cable of 15 mtrs length.

3 (ii) Size of interconnection cable from breaker terminal, CTs terminal to control relay panel is 2.5 Sq.mm. PVC copper control cable (un-armored).

- MECHANISM BOX CONTAINING :

- Operating mechanism

- Mechanical indicator for “ON” and “OFF” coupled to the Circuit breaker operating mechanism.

- Mechanical close and trip (with protective flap) lever/push button.

- Terminal blocks for control wiring and a spare terminal block (with 20% of the active terminals) (preferably nut & bolts type)..

- Operation Counter.

- Operating handle for manual charging of springs and for slow closing.

- 2 Nos. cable glands over and above those provided for control cables with suitable dummies.

- Not less than 4 numbers normally open and 4 normally lose spare auxiliary contacts over and above those required for normal operation.

- 250 V single phase AC Motor/Manual operated spring charging mechanism complete with electrical spring release coil, 2 Nos. shunt trip coil and 1 No. closing coil.

- Local – Remote selector switch.

- Earth bar (suitable for termination of 2 Nos. 50 x 6 mm class)

- 6 Nos. Terminal connectors for incoming and outgoing connectors.

- Set of 2 pole MCBs for AC and DC supply with different colours.

- 1 No. of reputed make anti-pumping relay.

3.	CONTROL AND RELAY PANEL :

Weather proof vermin proof control and relay panel shall be either structure mounted / floor mounted having equipped as follows:

- 3 ½ Digit LED Display CT operated digital A.C. Ammeter with Class of Accuracy 0.5 to suit the CT ranges indicated in Section-IV Schedule of materials. (110V AC Auxiliary supply) of size (96x96) mm.

- One ammeter selector switch with “R”, “Y”, “B”, “Neutral” and “OFF” position.

- One Heavy duty Pistolgrip type Control Switch for VCB trip/Neutral/Close positions with spring return to neutral position.

- One Red and one Green pilot LED lamps for indicating close and open positions respectively.

- One Yellow LED lamp for healthy trip indication with push button control.

- One white LED lamp for spring charged indication.

- One amber LED Lamp for auto-trip indication.

- One 3 phase 4 wire static HT Trivector CMRI Compatible as per TSSPDCL standards class 0.2S accuracy suitable scaled to work on 110 V AC 50 Hz            1 Amp to suit the CT ranges indicated in Section-IV Schedule of materials.

- Numeric Relays shall be of reputed make (drawn out type) with the following features.

a)	IDMT relay with three poles arranged for O/L and one pole for E/L with high set instantaneous elements for high fault currents for 33 KV Circuit Breakers.

- Two Nos. cable glands over and above those provided for control CT, PT, Control Circuit cables and auxiliary supplies (AC&DC) with suitable dummies.

- 3 ½ Digit LED Display digital A.C. Voltmeter with selector switch (Seven position) for 33KV Circuit Breakers (110V AC Auxiliary supply) of size (96x96) mm.

- One 3 Phase Mw meter and one 3 phase MVAR Meter to work on 110V AC                50 Hz 1 Amp and scaled to suit the ranges of CTs. (Size (96x96 mm)

- One set alarm bell and push button for acceptance of alarm.

- Necessary LT Fuses/MCBs for Control Circuit. Set of fine wiring with ferrules with standard code number of respective terminals and with suitable terminal connectors.

- 250 V three pin socket with plug & switch.

- Test terminal block with CT and PT terminals with links for testing ammeter and energy meter.(4W)

- Master trip relay of HR (fast acting)

- Trip circuit supervision & DC fail supervision relays are required.

- Stud terminal blocks (Bolt and nut type) for CT and PT control cables suitably wired with 6 Nos. spare terminals.

- One suitable copper earth strip of 12 x 3 mm size with adequate number of holes with suitable nuts and bolts.

NOTE : 	1.	All the instruments and relays to be proved on control panel shall be flush mounted unless otherwise specified. The relays are to be worked on 1 amp secondary current of CTs and with DC Voltage of 24 V

2.	All the indicating meters (Ammeter, Voltmeter, MW meter, MVAR meter) shall be of 144 x 144 or standard size and preferable of reputed make.

- 1 No. LED for TC1, through TS Relay, 1 No. LED for TC2 through TS relay.

- 1 No. plug point with switch (10A, 250 VAC)

- 1 No. Illuminator lamp with switch (40W, 250 VAC)

- 1 No. panel space heater with heater switch thermostat.

4.	CURRENT TRANSFORMERS.

Three numbers outdoor CTs as specified.

5. 	Terminals connectors suitable for Panther ACSR conductor for 33 KV and panther ACSR conductor for 11KV shall be supplied for Circuit Breaker (6 Nos.) and CT terminals                  (6 Nos.)

Suitable inter connection between circuit breaker terminals and CT terminals are to be provided.

Cables from circuit breaker and CTs to control panel shall be provided. As specified in the Section VI Schedule of equipment.

Note :	Other standard accessories which are not specifically mentioned but supplied with breakers of similar type and rating for efficient and trouble free operation shall be provided.

VII.	TESTS :

The Circuit breakers and current transformers shall be subjected to the following routine and type tests in accordance with the details specified in the relevant Indian Standards as amended from time to time or any other equivalent international standards.

- CIRCUIT BREAKER : IS 13118/IEC 62271-100 or  Latest version.

Copy of type test certificates shall be enclosed to the tender. The date of type test certificates shall not be later than 10 years from the date of tender opening.

  - ROUTINE TESTS :

- Measurement of resistance of the main circuits.

- Operation tests.

- One minute power frequency voltage dry withstand test on the circuit breakers.

- One minute power frequency voltage dry withstand test on auxiliary circuits.

  - TYPE TESTS :

- Temperature rise test for the main circuits.

- Measurement of resistance of the main circuit.

- Operation tests.

- Mechanical endurance tests (M2 class suitable for 10000 operations).

- Impulse voltage tests.

- One minute power frequency voltage dry withstand tests.

- One minute power frequency voltage wet withstand tests.

- Tests for short circuit conditions.

- Tests for short time current.

- Seismic switching duty test (0.6 g)

- Capacitor switching duty test.

1.3	ACCEPTANCE TESTS:

The inspecting officer shall carryout acceptance test on 10% of circuit breakers, randomly chosen from the offered lot.

The acceptance tests shall be as follows:

- Measurement of resistance of main circuit.

- Operation test.  This shall comprise five operation test cycles.

- One minute power frequency voltage dry withstand test on the circuit breaker.

- One minute power frequency dry withstand test on Auxiliary circuit.

- The method of carrying out the above acceptance tests shall be as per IS : 13118/1991.  Test parameters wherever applicable shall be as per this IS.

2. 	CURRENT TRANSFORMERS:

2.1.	The following Type tests as per IS 2705 (Latest version) shall be conducted and Type Test Certificates for the tests shall be enclosed along with the tender. The date of type tests shall not be later than Ten years from the date of tender opening.

- Short time current Test.

- Temperature rise test.

- Lightning Impulse Test.

- High Voltage Power frequency wet withstand voltage test.

- Determination of errors or other characteristics according to the requirements of the appropriate designation or accuracy class.

2.2	 ACCEPTANCE & ROUTINE TESTS: The following tests shall be conducted as per IS:2705: 1992.

- Verification of terminal marking and polarity.

- Power frequency dry withstand Test on primary & secondary windings.

- Over Voltage Inter turn test.

- Determination of errors or other characteristics according to the requirements of the appropriate designation or accuracy class.

VIII         SPECIAL GUARANTEE FOR CIRCUIT BREAKERS :

i)	The Circuit Breakers (total equipment) shall be guaranteed for satisfactory operation for a period of 10 years from the date of receipt at stores.

- All similar materials or removable parts of similar equipment shall be interchangeable with each other.

- DRAWING AND LITERATURE :

Drawings and technical literature of Breakers, Current Transformers and panels shall be enclosed to the offer, Tenders not accompanied by the above are liable to be rejected. These drawings and literature are to be supplied in duplicate copies along with each unit in the event of order and are to be housed in a proper weather proof enclosure on the rear of the control panel door. One set of reproducible drawings shall be supplied. Schematic wiring diagrams of the control circuits of the circuit breaker and control & relay panel shall be displayed (embossed on a plate/Laminated) on the doors of the circuit breaker, control cubicle and control & relay panel respectively.

- OVERALL DIMENSIONS AND FOUNDATION DETAILS:

The manufacturer shall give the necessary information as regards the overall dimensions of the circuit breaker and foundation details.

- PACKING :

All the equipments shall be packed in suitable crates with suitable steel bands so as to withstand rough handling and storage at destination.

SECTION – V

I.GUARANTEED TECHNICAL PARTICULARS FOR 33KV VACUUM CIRCUIT BREAKERS

(porcelain clad)

| 1. | RATED VALUES AND CHARACTERISTICS |  | As per TSSPDCL Requirement | As per bidder |
| --- | --- | --- | --- | --- |
|  | a) | No. of Poles | 3 |  |
|  | b) | Type | Outdoor Porcelain Clad VCB |  |
|  | c) | Rated Voltage | 33 KV/36 KV |  |
|  | d) | Rated Insulation-Level |  |  |
|  |  | i) Impulse withstand voltage | 170KV (peak) |  |
|  |  | ii) One minute Power frequency withstand voltage. | 70KV (rms) |  |
|  |  | iii) One minute Power frequency withstand voltage on Auxiliary wiring. | 2 KV (rms) |  |
|  | e) | Rated Frequency | 50 HZ |  |
|  | f) | Rated Normal Current | 1250 A |  |
|  | g) | Rated Cable charging current | 50A |  |
|  | h) | Rated (Single) Capacitor breaking current | 400 A |  |
|  | i) | Rated Small Inductive breaking current | As per IS-13116/1991 or IEC-62271/100-2008 |  |
|  | j) | Rated Symmetrical Short Circuit breaking Current and breaking capacity in MVA. | 25 KA (1500 MVA) |  |
|  | k) | Rated Transient Recovery Voltage. | As per IS : 13118/1991/IEC-62271-100/2008 |  |
|  | l) | Rated short Circuit making current | 62.5 KA |  |
|  | m) | Rated Operating Sequence | O-0.3Sec-Co -3Min-CO |  |
|  | n) | Rated duration of short circuit | 3 Sec |  |
|  | o) | Opening time and Break time (milli Sec.) | <40ms and <80ms |  |
|  | p) | Closing Time (Milli Sec.) | 100ms max |  |
| 2. |  | Whether type test certificate enclosed with tender | Yes |  |
| 3. | a) | Pressure maintained in vacuum chamber. | 10-6 torr |  |
|  | b) | Gap between the contacts in Vacuum. | 21 + or -2 mm |  |
|  | c) | Area of contacts. | Adequate |  |
|  | d) | The voltage to which the circuit breaker shall be capable of withstanding indefinitely across open contacts. | 36KV |  |
| 4. |  | Minimum Clearance in air |  |  |
|  | a) | Between Phases | 420mm |  |
|  | b) | Between Live parts to earth | 450mm |  |
| 6 | OPERATING MECHANISM OF CIRCUIT BREAKER AND ASSOCIATED EQUIPMENT : |  |  |  |
|  | 1. | Type of closing mechanism. | Spring-Spring, motor charged |  |
|  | 2. | Whether Circuit breaker is Fixed trip or Trip free. | Trip free |  |
|  | 3. | No. and type of auxiliary contacts (No. of spare normally open contacts and No. of spare normally closed contacts are to be indicated). | 4 N/O + 4 N/C Type : |  |
|  | 4. | Power requirement : |  |  |
|  |  | i) Closing coil | 300W(Max) |  |
|  |  | ii) Opening coil | 300W(Max) |  |
|  | 5. | Electrical service life : |  |  |
|  |  | i)Rated Current (times) | 10000 Nos.(Min) |  |
|  |  | ii) Rated interruption current (times) | 100 Nos.(Min) |  |
|  | 6. | Periodicity of maintenance for the following: For maintaining Vacuum in interrupting chamber Chamber. | _ |  |
|  |  | 1) For maintaining Vacuum in Interrupting chamber. |  |  |
|  |  | 2) For changing contacts. |  |  |
|  |  | 3) Other maintenance schedules if any. | _ |  |

II.	GUARANTEED TECHNICAL PARTICULARS FOR 33 KV CURRENT TRANSFORMERS                               Make : Vidyuth/Vishal Transformers/S.G.Electricals/Reputed make

| S.No | Description | As per TSSPDCL Requirement | As per bidder |
| --- | --- | --- | --- |
| 1 | Type | Single phase outdoor live tank oil cooled vacuum impregnated type |  |
| 2 | Manufacturer’s Type & designation | 33 KV Outdoor live tank oil cooled CT |  |
| 3 | Rated Voltage | 33 KV |  |
| 4 | Rated Primary current | 400-200-100 |  |
| 5 | Rated Secondary current | 1A |  |
| 6 | No. of cores (Secondary core details) | Three |  |
| 7 | Rated Output in VA | Core I : 15VA Core II : 5 VA Core III : PS |  |
| 8 | Class of Accuracy | Core I : 5P10 Core II : 0.2S Core III : PS |  |
| 9 | Accuracy Limiting factor | Core-1 :10 for protective core Core-II :Not applicable Core-III : Not applicable |  |
| 10 | Knee point voltage of PS cores | 40 I(Rct+10) |  |
| 11 | Maximum excitation current for PS cores. | 30mA at 0.25 Vk |  |
| 12 | Method of ratio change and secondary connection details & connection diagram. | Secondary Tapping |  |
| 13 | Secondary voltage | Not Applicable |  |
| 14 | Secondary Limiting Voltage | Not Applicable |  |
| 15 | short time current | 25 KA/3Sec |  |
| 16 | Rated current dynamic (Peak Value) | 62.5KA Peak |  |
| 17 | Rated continuous thermal current temperature rise over ambient. | 1.2 times continuous and 1.5 times for 3 sec |  |
| 18 | One minute power frequency Dry/Wet withstand voltage in KV (r.m.s) | 70KV Rms |  |
| 19 | 1/50 micro second Impulse withstand test voltage in KV (Peak) | 170KV Peak |  |
| 20 | One minute power frequency withstand test voltage on secondaries in KV (r.m.s) | 3KV Rms |  |
| 21 | Total weight of oil in KG | As per approved drawing |  |
| 22 | Total weight of in KG | As per approved drawing |  |
| 23 | Magnetization curve of CT core | - |  |
| 24 | Mounting details | As per approved drawing |  |
| 25 | Overall dimensions | As per approved drawing |  |

III.GUARANTEED TECHNICAL PARTICULARS FOR HT TRIVECTOR METERS

| Sl.No | Characteristics |  |
| --- | --- | --- |
| 1 | Makers name and country | Secure/L&T/Elster |
| 2 | Type of Meter/model | Static/As per supplier make |
| 3 | Accuracy class | 0.2s as per IS 14697/99/Meter PTR : 11KV/110V CTR : 400/1A |
| 4 | Power consumption for phase |  |
|  | i) Voltage Circuit | 1 Watts & 8 VA per phase |
|  | ii) Current circuit | Less than 1VA/Phase |
| 5 | Minimum starting current (%lb) | 0.1% Ib per IS 14697/99 |
| 6 | Parameters measured | 1. Lamp test |
|  |  | 2. Date & Time |
|  |  | 3. Active energy-kwh/Mwh import & Export |
|  |  | 4. Active Energy lad-KV Arh/MV Arh import & Export |
|  |  | 5. Active Energy lad-KV Arh/MV Arh import & Export |
|  |  | 6. Apparent energy –Kvah/Mvah import & Export |
|  |  | 7. Max. demand (00.00-24.00hrs) (KVA) |
|  |  | 8. Max. demand (00:00 24 hrs) occurance time |
|  |  | 9. Inst. Avg. power factor |
|  |  | 10.Aggregate Power factor |
|  |  | 11. Rising demand with Elapsed time (KVA/MVA) import & Export |
|  |  | 12. Cumulative MD resets |
|  |  | 13. Cumulative MD (KVA/MVA) import/export |
|  |  | 14. Inst. Phase Voltage – R,Y, B phase |
|  |  | 15. Inst. Phase Voltage – R,Y, B phase |
|  |  | 16. MD with 15 minutes integration |
|  |  | 17. Real time |
|  |  | 18. LED test |
|  |  | 19. Power off, Power fully On and Power partially On Periods |
| 7 | No of digits of display and height of character | 8 digits and 9mm height |
| 8 | P.F. range | 0 Lag – UPF – 0 Lead |
| 9 | Variation of voltage at which meter functions normally | -30% to + 20% |
| 10 | Particulars of read out |  |
|  | a) Continuous display | As per Sl.No.6 of above. |
|  | b) manually on display | 1. Supply frequency |
|  |  | 2. Present PT & CT status |
|  |  | 3. Last occurrence tamper ID |
|  |  | 4. Time and date of last occurrence |
|  |  | 5. Time & date of last tamper restoration |
|  |  | 6. Cumulative tamper occurrence counts |
|  | c) auto display parameters |  |
|  | i) Scrolling period | 10 Sec |
|  | ii) Display off period between two cycles | 2 Sec |
|  | d) With CMRI/RMR | As per technical specification |
| 11 | Details of Meter base and cover |  |
|  | a) Type of material | 1. base : Poly Carbonate 2. Top : Polycarbonate Transparent |
|  | b) Dimensions and weight | As per the make of the meter |
| 12 | Non volatile memory retention time in absence of power | 10 Years |
| 13 | Memory capacity (kB) | 32 KB |

| 14 | Details of tamper and fraud provisions |  |
| --- | --- | --- |
|  | a) On display | Yes, tamper & fraud status with last occurrence & restoration tamper ID with date & time. Cumulative tamper occurrence count will also provide on meter display. |
|  | b) With meter reading instrument and data transfer | Yes Provided |
|  | c) Detailed explanation how the tamper detection made is furnished or not? | Tamper information: R,Y,B phase CT reversal Phase sequence error Voltage imbalance, Magnet sense. |
| 15 | Guarantee for satisfactory operation of meter | 5 Years from the date of receipt of material at destination stores by the consignee in good condition. |
| 16 | Standards to which the meter confirms | IS 14697 : 1999 |
| 17 | Overload capacity | - Continuous 1 Amps - B. Momentary – 20 Amps (1 Second) |
| 18 | Dynamic range | 0.1% Ib to 200% Ib (The offered meter are long range meter hence Imax is equivalent to 200% of Ib) |
| 19 | a) Meter terminal block having sailable extended terminal cover | Yes |
|  | b) connection diagram inside the terminal cover | Yes |
|  | c) Maximum safe current the terminals and screws shall carry. | Yes |
| 20 | Change in errors (accuracy) due to variation in voltage, frequency and temperature to be furnished | Within the limits specified in relevant standards |
|  | a) voltage |  |
|  | i) +20% to +10% |  |
|  | ii) +10% to -10% |  |
|  | iii) -10% to -20% |  |
|  | iv) -20% to -30% |  |
|  | b) Frequency variation |  |
|  | i) 50 +10% HZ |  |
|  | ii) 50 +5% HZ |  |
|  | c)Temperature |  |
| 21 | Sealing of the meter (No of sales) |  |
|  | a)Meter cover | Yes |
|  | b) Terminal Block cover | Yes |
|  | c) others, if any, | Nil |
| 22 | Whether meter carries any certification mark. | BIS –IS : 14697/1999 |
| 23 | Self diagnostic features (provide details) | Power on memory Integrity check |
| 24 | Principle of operation (Provide details) | Provided by the supplier |
| 25 | Any additional measuring parameters | Nil |

IV. GUARANTEED TECHNICAL PARTICULARS for NON DIRECTIONAL NUMERICAL 3 O/C + 1E/F

(IDMTL WITH HIGHSET)  RELAYS 1A & 5A (MULTIPLE SECONDARY CURRENT OPTION)

| CT Input Rating |  | - |  | 1A &5A (Multiple secondary current Option) |
| --- | --- | --- | --- | --- |
| Frequency |  | - |  | 50 Hz |
| Digital status Digital Inputs Digital Outputs |  | - - |  | 2Nos 4Nos |
| Protection Settings Phase Fault Earth Fault Highset Phase fault Highset Earth Fault P/F Time Multiplier(IDMTL) E/F Time Multiplier(IDMTL) P/F DTL E/F DTL P/F Highset DTL E/F Highset DTL Reset Time |  | - - - - - - - - - - - |  | 20% to 400%(in step of 0.05xIn) 5% to 250%(in step of 0.05xIn) 50% to 4000%(in step of 0.05xIn) 5% to 1500%(in step of 0.05xIn) 0.01 to 1.5sec( in step of 0.005sec) 0.01 to 1.5sec( in step of 0.005sec) 0.1 to 150sec (in Step of 0.01sec) 0.03 sec to 150sec (in Step of 0.01sec) 0.02sec to 20sec (in Step of 0.01sec) 0.02sec to 20sec (in Step of 0.01sec) 0 Sec to 20 Sec |
| Curve selection provision for IDMT 3 Sec. & 1.3 Sec(Extreme inverse, very inverse, Normal inverse, Highset) |  |  |  |  |
| Output Contacts The Relay has the following output contacts - Common Trip and Alarm - Configurable outputs | - - |  | 1 N/O +1 N/C 3 N/O |  |
| Contact Rating Carry Continuously Breaking capacity Making capacity | - - - |  | 6A AC 230V rms /DC 6A 24V & 220V Maximum 2000 VA Maximum 8A |  |
| LED |  |  | 8 LEDs to view pickup and trip action |  |
| Push Buttons |  |  | For setting the relay |  |
| Password facility |  |  | Required |  |
| Circuit Breaker failure protection |  |  | Required |  |
| Communication |  |  | RS 485 with Modbus |  |
| LED Indication | - - - |  | LED ON LED PHASES L1,L2,L3 LED TRIP INDICATION(I>,I>>,Io>,Io>>) |  |
| 16x2 Bright Alphanumeric LCD display for settings, readings and fault tripping data of minimum number 10 reports( with date and time stamping) |  |  |  |  |
| Measurements |  |  | L1,L2,L3 and Earth |  |
| Burden AC Current input 5 A Rating 1 A Rating | - - |  | < 0.1VA < 0.2 VA |  |
| Auxiliary input Quiescent (typical) |  |  | 3W (DC) 12VA (AC) |  |
| Environmental Temperature Operating range Storage range Humidity Transient Over voltage |  |  | As per IEC -200C to + 700 C -400C to + 850C As per IEC As per IEC 56 days at 400C and 95% RH |  |
| 5Kv, 1.2/50 s, 0.5J between all terminals and earth or between any two terminal without damage or flashover |  |  |  |  |
| Insulation 2.0 KV rms for 1 min between all terminal and earth 2.0 KV rms for 1 min between independent circuits 1.0 KV rms for 1 min across normally open contacts | - |  | As per IEC |  |
| High frequency Disturbance 2.5KV Common (Longitudinal) mode 1.0KV Series (Transverse) mode Electrostatic Discharge 6 KV Contact Discharge 8 KV Air Discharge | - - |  | As per IEC As per IEC |  |
| Radio Frequency Interference 20MHz to 1000MHz, 10 V/m | - |  | As per IEC |  |
| Fast Transient 2KV 5/50ns, 2.5kHz repetitive Vibration (Sinusoidal) Shock and Bump |  |  | As per IEC As per IEC As per IEC |  |
| Mechanical Classification Durability | - |  | 100 operations |  |
| The relay to be supplied should also have the following features The relay should have the communication port for compatibility of RS 485 with modbus RTU. |  |  |  |  |

ANNEXURE – I

STATIC TRIVECTOR METERS FOR USING ON 33 KV FEEDERS WITH VCBS.

Three phase 4 wire Static Trivector Meter of reputed make of class 0.2S accuracy suitable to work on 110V/√3 AC, 50 Hz, -/1A for balanced and as well as unbalanced loads at all power factors i.e., Zero-lag-Unity-Zero lead to suit to be installed on 33 KV outdoor feeder panels and to suit the CT ranges indicated in Section-IV Schedule of materials. The meter should be capable of performing function of metering In all 4 quadrants, load survey etc. The meter shall conform to latest version of IS: 14697/99 CBIP Technical report 88/IEC 687 for accuracy and environmental and other relevant standards.

The meter should be capable of measuring the following electric parameters of poly phase supplies in all 4 quadrants at all power factors lagging or leading.

1.	KWH	Import and export

2.	KVRH	Import and export (lag & lead)

3.	KVAH	Import and export

4.       	Voltage of individual phases.

- Currents in each individual phase.

- Average Power factor.

- Maximum demand (15 Minutes Integration)

- Cumulative demand with No. of resets.

- Real time.

- Power off and power fully on and power partially on periods.

The meter should be capable of recording the full supply period, partial supply period and no supply period and display the same in separate tables with date, time and duration.

The meter should log the following parameters with 15 min, integration for the last             36 days in its memory card  and it should be possible to transfer this data on to a base computer station through a DOS based hand held CMRI.

Parameters for logging shall be in import and export modes

- KWH

- Currents in all the three phases

- KVARH

- Voltage in all phases.

The base computer shall give complete details of load survey particulars both in numeric data form and in graphic form. Necessary software for invoking the base computer station should be provided.

The meter shall be provided with a galvonically isolated optical communication port (such as IEC-1107, PACT, ANSI etc.,) with removable cover and with locking arrangement so that it can be easily connected to a CMRI for data transfer or transfer of data through remote metering device such as modem/ multi flexer etc.  The optical communication port shall also have sealing provision.

The meter shall also be provided with a sealable RS 485 port with MODBUS Open protocol which can used for AMR metering along with  9 pin D-type male connector so that it can be easily connected to a hand held meter reading instrument for data transfer or subsequently hooked to remote metering device such as modem etc. Necessary protocol software should be loaded into the CMRI and Base computer station of the Board for the purpose of reading and programming the specific make(s) of static meters and accepting data  from hand held terminal/CMRI and processing, generating reports and won loading instructions from the base computer station to CMRI respectively.

The supplier is responsible for maintaining the security of the data extracted from the meters using manufacturers specific algorithms in the software upto down loading to the base computer station.

The meter shall have minimum legible 8-digit display of LCD. The display shall be digital type with non destructive readout and shall be possible to display legend for identification of display. The meter shall have facility of auto display mode where all parameters automatically scroll within the specified time. The number of parameters and the scrolling period shall be field programmable. It shall also be possible to read the parameters by a manual switch.

The non volatile memory shall have a minimum retention time of 12 years.

NOTE : All protocols are to be handed over to purchaser in advance and the memory map of the meter shall be furnished along with the tender.