SPECIFICATION NO. STN-20/2014

TECHNICAL SPECIFICATION FOR 33KV POTENTIAL TRANSFORMERS, 0.2 CLASS

1. SCOPE: - The specification covers the design, manufacturer, assembly testing at manufacturer’s works and supply and delivery at destination of outdoor oil immersed 33kV Voltage Transformers for using consumer services metering purpose.

2. 	STANDARDS:   The equipment shall conform in all respects to the latest version of relevant IS indicated below as applicable.

i)	Voltage Transformers 				:  IS 3156 (Part-I & II).

ii)	Oil						:  IS 335.

iii)	Galvanization 					:  IS 2633.

iv)	Primary Terminals. 				:  IS 10601.

The bidder shall go through the above IS thoroughly before making his offer.

3.  CLIMATIC CONDITIONS:   The climatic conditions under which the equipment shall operate satisfactorily are as indicated at page (12) 0f General Terms and Conditions for supply of materials.

4.   33 KV POTENTIAL TRANSFORMERS:

4.1 TYPE:  The Voltage transformers shall be outdoor oil immersed self cooled vacuum impregnation type suitable for operation in 3Ph. 33 KV  50 Hz solidly grounded system under the normal service conditions specified in IS 3156 and as indicated, in the Section – IV “ Schedule of Materials”.

4.2.    The Voltage transformer shall have the following ratings.

a)   Rated voltage: 					33 KV

b)   No. of Phases/ connection: 			Single Ph. 		.

c)   INSULATION LEVEL:

i)   Nominal system voltage. 			33 KV

ii)  Highest system voltage. 			36 KV

iii) Standard Impulse withstand voltage. 	 170 KV

iv) One minute power frequency

Withstand voltage.

a)   Primary				70 KV

b)   Secondary. 			 3 KV

v)  Rated voltage factor and 			1.2 times continuous and

Corresponding rated time. 		1.5 times for 30 seconds

d)   Rated transformation ratio :			As indicated in Sec. IV

“Schedule of Materials”.

i)	Class of Accuracy		    	0.2		 	  		    	ii)	Rated Burden	/ Phase. 	    	10 VA

e)	Type of Transformer. :		     		Earthed

f)    	No. of windings/phase.		    	One

4.3	Each voltage transformer shall be capable of carrying without injury continuous burden of 25% above the rated burden in respect of 33 KV Potential Transformers.

5.   CONSTRUCTION:

5.1.	The core shall be high grade non-ageing electrical silicon laminated steel of low hysteresis loss and high permeability to ensure high accuracy, at both normal and over current/ voltage.

The secondary terminals shall be brought into a compartment on one side of voltage transformers for easy access. The secondary taps shall be adequately reinforced to withstand normal handling, without damage.

The voltage transformers shall be suitable for mounting on steel structures or concrete pedestals. The necessary flanges, bolts, etc. for the base of the Potential Transformers shall be supplied and these shall be galvanized. The tank and other metal parts shall be galvanized.

All winding shall be of insulated high grade Electrolytic copper wire and the manufacturing  of the units shall be done in completely closed and air-conditioned room otherwise Fiber glass insulation sleeves are to be provided for primary winding.  Details of winding and core shall be furnished.

The Potential Transformers shall be completed in all respects with first filling of oil conforming to IS 335 and with oil level indicator with minimum/maximum oil levels.  The top cover and terminal box cover should be such that rain water does not enter even through the gaskets.

Potential Transformers tank MS sheet thickness required 3.15mm(min) and Secondary terminal shall be provided with nut & bolts.

5.2.	PRIMARY & SECONDARY TERMINALS:  Primary terminals of Potential Transformers to which the line connections are to be made shall have dimensions as per IS:10601:1983.

The secondary terminals shall be brought out into suitable compartment, which shall have a removable cover. The terminal box with the cover closed and tightened and the cable/conduit in position when supplied shall have a degree of protection conforming to                  IP 54 of IS:2147.

5.3. TERMINAL AND EARTH CONNECTORS:  Terminal connectors suitable for Panther ACSR Conductor shall be supplied.   Suitable earth connectors for earthing connections shall also be supplied.

Primary terminal diameter should be 20mm(min), Primary brass terminal (External) lengths should be 50mm(min) and Aluminum stud holder to be provided with bimetallic clamp.

5.4.	EARTHING:   The earthing terminals shall be adequate size protected against corrosion and metallically clean and identified by means of the sign marked in a legible and indelible manner on or adjacent to the terminals.

5.5.	SEALING ARRANGEMENT: Provision for sealing secondary terminal compartment, primary ratio change strips (if any) and tank effectively shall be made such that no fraud etc.  such as tampering of the ratio or circuit (current/voltage) is possible.   The holes provided for the above sealing provision shall be of adequate size and pass the sealing wire of about                14 SWG.

5.6.   NAME / RATING PLATE:  Each Potential Transformer shall have the following particulars indelibly marked on it or on a label permanently secured to it or its casing.

Manufacturer’s name.

- Year of manufacture.

- Manufacturer’s Sl.No. and / or type designation.

- Rated transformation ratio.

- Rated frequency.

- Rated output and the corresponding accuracy class.

- Highest system voltage.

- Rated voltage factor and corresponding rated time.

- Type of transformer.

- Number of phases and method of connection.

5.7.1.	Each instrument Transformer shall be provided with prismatic type oil sight window at suitable location so that the oil level is clearly visible with naked eye to an observer standing at ground level.

5.7.2.	The units shall be vacuum filled with oil, after processing and thereafter hermetically sealed to eliminate air and moisture from entering the tank.

5.7.3.	Oil filling and / or oil sampling cocks if provided to facilitate factory processing shall be permanently sealed before dispatch of the instrument transformer.

6.	TESTS:

6.1.	33KV POTENTIAL TRANSFORMERS:

6.1.1.	 TYPE TESTS:  The following Type Tests as per IS: 3156 (Latest Version) shall be conducted and Type Test Certificates for the Tests carried out on Prototype of same specification shall be enclosed with the tender. The date of type tests shall not be later than TEN years.

- High voltage Power frequency wet withstand voltage test.

- Determination of errors according to the requirements of the appropriate accuracy class.

- Temperature rise test.

- Impulse Voltage test.

6.1.2	ACCEPTANCE & ROUTINE TESTS:    The following shall be conducted as per IS:3156 (Latest version).

- Verification of Terminal marking and polarity.

- Power frequency/ dry withstand tests on primary windings.

- Power frequency dry withstand tests on secondary windings.

- Determination of errors according to the requirements of the appropriate accuracy class.

7.   INSPECTION:    All acceptance tests shall be conducted at the time of inspection and inspection shall be made at the place of manufacturer unless otherwise specifically agreed upon by the manufacturer and purchaser at the time of purchase.  The manufacturer shall afford the inspector representing the purchaser all reasonable facilities without charges to satisfy him that the material is being furnished in accordance with the specification.

The purchaser has the right to have the tests carried out at supplier’s cost by an independent agency whenever there is a dispute regarding the quality of supply.

8.  GUARANTEED TECHNICAL PARTICULARS:  The technical particulars as per IS (Latest Version) shall be guaranteed and guaranteed technical particulars as per Annexure – I shall be furnished by the bidder along with his offer.

9.   DRAWINGS & LITERATURE:  Drawings and Technical Literature of Potential Transformers shall be enclosed to the offer.  Sectional view and dimensions for all parts to the extent possible shall be indicated in the drawings.  Tenders not accompanied by the above are liable to be rejected.  These drawings and literature are to be supplied @ 2 copies along with each unit in the event of order.

10.   OVERALL DIMENSIONS AND FOUNDATION DETAILS:  The manufacturer shall give the necessary information as regards the overall dimensions of the transformer and foundation details.

11.   SCHEDULE OF REQUIREMENTS, DESIRED DELIVERY AND PRICES:

11.1 The schedule of requirements and desired deliveries are indicated in Sec. – IV.

11.2 The schedule of prices shall indicate online only.

Note:   The bidder shall indicate the source of all materials.   He shall also indicate the name of the supplier and make of conductor, Transformer oil Electrical Steel Laminations, Construction Steel etc.

Sd/--

CHIEF GENERAL MANAGER/P&MM

ANNEXURE – I .

GUARANTEED TECHNICAL PARTICULARS.

33 KV POTENTIAL TRANSFORMERS:

| 1. | Name and Address of Manufacturer. | CPDCL requirement | As per bidder |
| --- | --- | --- | --- |
| 2. | Manufacturer’s Type & Designation. |  |  |
| 3. | Nature of service | Outdoor |  |
| 4. | Type of Cooling. | Oil cooled |  |
| 5. | System Characteristics. - Rates System Voltage. - Highest System voltage. - Rates system frequency. - Nature of neutral earthing. | 33KV 36KV 50HZ Earthed |  |
| 6. | Rated Voltage ratio. | 33KV/√3/110V/√3 |  |
| 7. | Winding connections. | Star/Star |  |
| 8. | Rated burden. | 10 VA |  |
| 9. | Class of accuracy. | 0.2 |  |
| 10. | Polarity. | - |  |
| 11. | Rated voltage factor and time. | 1.2 Cont & 1.5 for 30sec |  |
| 12. | Limits of ration and phase angle error | As per IS:3156 |  |
| 13. | Temperature rise of top oil at 1.1 times rated primary voltage with rated secondary burden. | Within the limit as specified in IS |  |
| 14. | H.V Insulator characteristics. - Type. - Make - Electrical Characteristics. - Total Creepage distance. | Outdoor _ As per IS 900mm(minimum) |  |
| 15. | One minute power frequency dry withstand test on primary winding. | 70KV rms |  |
| 16. | One minute power frequency withstand test on secondary winding. | 3KV rms |  |
| 17. | High Voltage impulse withstand test on primary windings. | 170KV(peak) |  |
| 18. | Oil : - Specification. b) Quantity for first filling. | IS-335 _ |  |
| 19. | Total weight of PT with oil. | As per approved drawings |  |
| 20. | Reference specification to which the equipment conform. | IS-3156/92 with latest amendments |  |
| 21. | Outline dimensional drawing with mounting details. | As per approved drawings |  |
| 22. | The Potential transformers shall carry 25% above the rated burden continuously without injury in respect of 33 KV PTs | Should be complied |  |

SIGNATURE OF THE TENDERER.

GUARANTEED TECHNICAL PARTICULARS FOR NEW TRANSFORMER OIL

CONFIRMS TO  IS-335/93 OR LATEST VERSION.

| Sl.No | Details | CPDCL requirement | As per bidder |
| --- | --- | --- | --- |
| 1. | Appearance | Clear and transparent and free from suspended matter and sediments |  |
| 2. | Density, gm/cm at 27 Deg. C | 0.835 |  |
| 3. | Kinetic viscosity at 27 Deg. C | 25 |  |
| 4. | Interfeacial tension, N/m | 0.04 |  |
| 5. | Flash pont, PMCC, OC, Min. | 165 |  |
| 6. | Pour point, OC | (-) 18 |  |
| 7. | Neutralization value |  |  |
|  | a). Total acidity | 0.01 |  |
|  | b). Inorganic acidity | NIL |  |
| 8. | Corrosive sulphur | Non-Corrosive |  |
| 9. | Break down voltage, ms, Kv (Min.) |  |  |
|  | a) Non untreated | 30 |  |
|  | b) After treatment | 60 |  |
| 10. | Dielectric dissipation factor (Tan Delta at 90 Deg. C) (Max.) | 0.002 |  |
| 11. | Specific resistance (resistivity) |  |  |
|  | a) At 90 Deg. C (Min.) Ohm-Cm | 100 x 1012 |  |
|  | b) At 27 Deg. C (Min.) Ohm –Cm | 3000 x 1012 |  |
| 12. | Oxidation stability |  |  |
|  | a) Neutralization value after oxidation (Max.) | 0.01 |  |
|  | b) Total sludge, after oxidation (Mx.) | NIL |  |
| 13. | Ageing characteristics after accelerated ageing (open breaker method with copper catalyst) 96 Hrs. as per ASTMD 1934-1978 |  |  |
|  | a) Specific Resistance (resistivity) |  |  |
|  | i) At 27 Deg. C (Min.) Ohm-cm | 2.5 x 1012 |  |
|  | ii) At 90 Deg. C (Min.) Ohm-cm | 0.2 x 1012 |  |
|  | b) Dielectric dissipation factor (Tan delta) at 90 De. C (Max.) | 0.20 |  |
|  | c) Total acidity (Max.) | 0.05 |  |
|  | d) Total sludge value (Max.) | 0.05 |  |
| 14. | Presence of oxidation inhibitor | NIL |  |
| 15. | Water content (Max.) | 30 ppm |  |

SIGNATURE OF THE TENDERER