Specification No.STN-1090/2023

Amendment-II

| Sl. No. | Existing | Clarification |
| --- | --- | --- |
| 1. | Guaranteed Technical Particulars Page No. 41 Cable entry Exit arrangement. a) Incoming : 4 Nos. 48mm Dia PVC glands Provided at bottom. | Cable entry Exit arrangement. a) Incoming : 4 Nos. 48mm or 50mm Dia PVC glands Provided at bottom. |
| 2. | Terminal Thickness : Drawing | 1. The Fuse contacts should be of 3mm thickness and at T2 extra thickness of 3mm copper strip of 34 mm x 70mm strip shall be inserted. Total 12 Nos. 2. The Bi-metal strips of 30x30x1 mm shall be provided. Total 12 Nos. at HRC Fuse base terminals. |
| 3. | Cl.No. 2 Page No. 36 6 Nos. 400A, 500V porcelain fuse bases of standard make confirming to IS 13703 Cl. No. 3, Page No.37 The base of the HRC Fuse shall be of non-tracking, heat resistant insulating material of Dough Moulding Compound (DMC) of D3Grade as per IS:13411/1992 | 6 Nos. 400A, 500V porcelain fuse bases of standard make conforming to IS 13703 Shall be considered |
| 4. | Qualification Requirement Page No. 34 One set of Type Test Certificates shall be furnished. The type tests must have been conducted on the offered material as per IS 13410:1992 for SMC material and as per IS 14772 for box in NABL Accredited Laboratories with the latest revision. The date of type tests shall be not be older than 3 years as on date of tender opening. The Bids received without type test reports will be treated as Non-Responsive. | One set of Type Test Certificates shall be furnished. The type tests must have been conducted on the offered material as per IS 13410:1992 for SMC material and as per IS 14772 for box in NABL Accredited Laboratories with the latest revision. The date of type tests shall be not be older than 3 years as on date of tender opening. The Bids received without type test reports will be treated as Non-Responsive. The type test reports for fuse base as per IS 13703 mentioned in the tender document conducted in any NABL Accredited Laboratories shall be submitted on receipt of purchase order i.e., along with GTP and drawings without affecting the delivery schedule of the TSSPDCL. An undertaking in this regard should be submitted along with the bid document. However, the sample to be submitted as per the tender specification |

All other terms and conditions of the tender specification remain unaltered.

-sd-

CHIEF GENERAL MANAGER/P&MM