##### TENDER SPECIFICATION

## STN-943/2022

## FOR

##### THREE PHASE LTCT METERS WITH 100/5A of 0.5S Accuracy CTR WITH 4 CTS IN PP  BOX WITH 	NET-METERING FEATURES.

TABLE OF CONTENTS

SECTION	DESCRIPTION			    		PAGE NO.

I   		Notice inviting bids					        	4-6

II		Salient Features of the Bid				        	7

III		General Terms and Conditions Of Contract		        	8-33

IV		Schedule of Requirements					34

V		Qualification Requirements					35-36

VI		Technical 					                    	37-64

VII		  Sample Forms

1)	Bid Form			                    			65

2a) 	Bid Security Form						66

2b)	Performance Security Form				      	67

3)	Contract Form							68-69

4)	Performance Statement                                                       		70

5)	Details to be furnished by the Manufacturer (FORMAT-A) 	71

6)      	Schedule of deviations (Technical & Commercial)             	 	72-73

7)	Declaration Form						 74

NOTE:

1.	Payment terms, Delivery period, Performance Bank Guarantee, Taxes and Duties” should be in line with the terms and conditions of the specification. If any bidder does not meet any one of the conditions, such tender will not be considered. Please note that the conditional offers are also not considered. Hence the bidder shall submit the tender in line with the terms and conditions of the specification.

2.	The bidders shall check the website www.tssouthernpower.com and www.tender.telangana.gov.in for amendments, if any, upto one day prior to the date of tender opening. The amendments shall be binding on the bidders.

3.	The purchaser will not be responsible for any damage that may be caused to the samples at any time.

4.	The bidder shall furnish required Bid Security amount and validity as per specification.  If the bidder fails to furnish bid security amount and bid validity as stipulated in the specification, such tender bid will not be considered for further evaluation.

5.	The prospective bidders shall attend the pre-bid meeting (date and time in NIT) for any queries.  The discussed queries shall be submitted in the form of a letter during pre bid meeting or within 24 hrs of pre bid meeting.  Any new queries received after pre bid meeting are not liable to be considered.

6.	The bid evaluation will be carried out based on the documents uploaded through www.tender.telangana.gov.in against this tender.

7. 	The Bids received with any details pertaining to prices in the offline mode will be liable for rejection.

8.	In e-procurement commercial stage, if F&I charges are applicable then mention whether F&I charges entered are exclusive/inclusive of GST in the remarks section. If not mentioned in remarks, F&I charges will be considered as inclusive of GST.

9.	EMD Exemption is considered only for Government Firms.

Ph   : 040 – 23431448, 23431033.

Fax : 040 - 23431034.

CHIEF GENERAL MANAGER (P&MM)

TSSPDCL

| Energy Saved is |  | SOUTHERN POWER DISTRIBUTION COMPANY OF TELANGANA LTD. 4th Floor, Corporate Office, Mint Compound, Hyderabad |
| --- | --- | --- |

Tender Notice

TSSPDCL intends to float tenders for procurement of (a) 1Ph 5-30A IRDA 1.0C Net Meter in PP Box (b) 3Ph 10-40A IRDA 1.0C Net Meter in PP Box, (c) 3Ph LTCT100/5A 0.5S4CT Net Meter in PP Box (d) LT TVR 200/5A meters (4 CTS-0.5S) DLMS Protocol without Box (e) LT TVR 100/5A Meters, 0.5S (CAT-C) with DLMS & IRDA without  box,            (f) LT TVR 100/A 0.5S (CAT-C) meter with DLMS & IRDA with box, (g)  LT TVR 200/5A Meters (4CTs-0.5S) with DLMS & IRDA with  box (h) 100 Sq.mm AAA Conductor and               (i) GI Stay Wire 7/3.15 mm (10 SWG) on e-tender platform.

For further details, please visit www.tssouthernpower.com and www.tender.telangana.gov.in

Phone: 040-2343 1033, 1448, 1360, 1035

Sd/-

CHIEF GENERAL MANAGER (P&MM)

(P&MM)

ONLINE VERSION

Tender Notice No : STN-943/2022

| Notice Inviting Tender Details |  |  |
| --- | --- | --- |
| S.No | Description |  |
| 1 | Department Name | TSSPDCL |
| 2 | Office | Purchases & Material Management Wing, Corporate Office, TSSPDCL |
| 3 | Tender Number | STN-943/2022 |
| 4 | Tender Subject | Three phase LTCT meters with 100/5A of class 0.5S accuracy CTR with 4 CTs in PP Box with Net-metering features. |
| 5 | Delivery Schedule | The supplies shall commence in 45 days and complete within 3 months from the date of receipt of purchase order (For trial orders it is in proportion to the quantity quoted) |
| 6 | Tender Type | Open |
| 7 | Tender Category | NA |
| 8 | Bid Security (INR) | (i) 2% of the Ex-works quoted value (plus with GST @18%) (or) (ii) Exemption letter of Bid Security in case of Govt. firms. |
| 9 | Bid Security Payable to | In the form of DD in favour of Pay Officer/TSSPDCL / Hyd or BG from Nationalized/Scheduled Bank as per format 2(a). The validity of the bank guarantee shall be upto bid validity +45 days from the date of tender opening. |
| 10 | Processing Fee (INR) | NIL |
| 11 | Transaction Fee | Transaction fee: All the participating bidders who submit the bids have to pay an amount @ 0.03% of their final bid value online with a cap of Rs.10,000/- for quoted value of purchase upto Rs.50 crores and Rs.25000/- if the purchase value is above Rs.50 crores & service tax applicable as per GST as levied by Govt. of India on transaction fee through online in favour of M/s. TSTS. The amount payable to M/s. TSTS is non refundable. Corpus Fund: Successful bidder has to pay an amount of 0.04% on quoted value through demand draft in favour of Managing Director, TSTS, Hyderabad towards corpus fund at the time of concluding agreement. |
| 12 | Transaction Fee Payable to | TSTS, Hyderabad |
| 13 | Date & time of pre-bid meeting with manufacturer | 27-08-2022 at 11:30Hrs |
| 14 | Schedule Sale opening date | 19-08-2022 from 17:30 Hrs |
| 15 | Schedule Sale closing Date | 07-09-2022 Upto 17:00 Hrs. |
| 16 | Bid Submission Closing Date & time | 08-09-2022 Upto 12:00 Hrs |
| 17 | Bid submission | On Line |
| 18 | Pre-Qualification& Technical Bid Opening Date (Qualification and Eligibility Stage and Technical Bid Stage) | 08-09-2022 at 15:00 Hrs. |
| 19 | Price Bid Opening Date (Financial Bid Stage) | 12-09-2022 at 12:00 Hrs |
| 20 | Place of Tender Opening | O/o Chief General Manager/P&MM TSSPDCL, 4th Floor, Corporate Office, Mint Compound, Hyderabad – 500 004. |
| 21 | Officer Inviting Bids/ Contact Person | Chief General Manager/P&MM/TSSPDCL/HYDERABAD |
| 22 | Address/E-mail id | O/o. Chief General Manager/P&MM TSSPDCL, 4th Floor, Corporate Office, Mint Compound, Hyderabad – 500 004 |
| 23 | Contact Details/Telephone, Fax | Ph. No. 040-23431448, 040-23431319. Fax No. 040-23431034 |
| 24 | Eligibility Criteria | As per Section VI |
| 25 | Procedure for Bid Submission | Bids shall be submitted online on www.eprocurement.gov.in platform - The participating bidders in the tender should register themselves free of cost on e-procurement platform in the website www.eprocurement.gov.in. - Bidders can log-in to e-procurement platform in Secure mode only by signing with the Digital certificates. - The bidders who are desirous of participating in e-procurement shall submit their technical bids, price bids as per the standard formats available at the e-market place. - The bidders should scan and upload the following documents in support of technical bids. The bidders shall sign on all the statements, documents certificates uploaded by him, owning responsibility for their correctness/authenticity: a) Bid Security should be furnished i) In the form of DD in favour of Pay Officer/TSSPDCL/ Hyderabad (or) Alternatively BG from Nationalized/Scheduled bank in favor of Chief General Manager/P&MM/TSSPDCL/Hyd as per format-II enclosed (or ) ii) If exempted give details of Bid Security Exemption (in case of Govt. Organization) b) Quantity offered c) Proof of manufacturer-SSI, Department of Industries, Govt. of India Enterprise etc d) Latest “Sales Tax Clearance Certificate” e) Financial Turnover certified by CA for last 5 years f) Details of previous supplies along with PO copies and delivery challan copies for qualification requirement as per tender document. g) Performance Certificates issued by Head of Purchasing Authority (as per spec) h) Copies of relevant purchase order copies mentioned in the performance certificates in support of the above. i) Drawings, Guaranteed Technical Particulars of the product, other relevant documents attached to the bid. j) BIS certificate k) ISO certification l) Type Test Certificates in full shape m) Duly filled and signed proforma as per Format A 6. The rates should be quoted in online only |
|  |  | 7. After uploading the documents the copies of the uploaded statement, certificates, documents, original Demand Drafts in respect of processing fee, testing charges and Bid Security (except the Price bid/offer/break-up of taxes) are to be submitted by the bidder to the Chief General Manager/ P&MM/ TSSPDCL so as to reach before the date and time of opening of the technical bid. Failure to furnish any of the uploaded documents, certificates, before the date and time of opening of technical bid will entail in rejection of the bid. The Department shall not hold any risk on account of postal delay. Similarly, if any of the certificates, documents, etc., furnished by the tenderer are found to be false / fabricated / bogus, the bidder will be disqualified, blacklisted, action will be initiated as deemed fit and the Bid Security will be forfeited. 8. The department will not hold any risk and responsibility regulating non-visibility of the scanned and uploaded documents. 9. The Documents that are uploaded online on e-market place will only be considered for Technical Bid Evaluation. 10. Important Notice to Contractors, Suppliers and Department users (i) In the endeavor to bring total automation of processes in e-Procurement, the Govt. has issued orders vide G.O.Ms.No. 13 dated. 5.7.2006 permitting integration of electronic Payment Gateway of ICICI/HDFC Banks with eProcurement platform, which provides a facility to participating suppliers/ contractors to electronically pay the transaction fee online using their credit cards. |
| 26 | Rights reserved with the Department | TSSPDCL reserves the right to accept or reject any or all of the tenders received without assigning any reasons therefore. The TSSPDCL also reserves the right to split the tender and place orders on more than one tenderer at its discretion |
| 27 | General Terms and Conditions | As per tender documents. |

SECTION - II

SALIENT FEATURES OF THE BID

Superscription on the Tender Cover

Specification No				: STN-943/2022

Material	: Three phase LTCT meters with 100/5A of class                                                 0.5S accuracy CTR with 4 CTs in PP  Box with  Net-metering features.

Officer to whom the bid will be addressed	: CGM/P&MM, Corporate Office/TSSPDCL/Hyd

Superscription on the bid cover and

the outer envelope				:

- Specification No.		                : STN-943/2022

- Due date and time for online

& hard copy submission                   :  08-09-2022 at 12:00 Hrs

- Date and time of online opening    : 08-09-2022 at 15:00 Hrs

- Payment of bid security

i) If paid give details: DD No._____Dt.___ for Rs.______

ii) If exempted give details

- Payment of testing charges DD No._____Dt.___ for Rs.______

f. Whether 90 days validity offered ………(yes/no).

g. Whether bid is made accepting payment terms Clause….(yes/no).

h. Whether delivery is as per delivery schedule indicated….(yes/no)

i. Whether the sample (if specified) has been enclosed/sent…(yes/no)

j. Whether the quotation is in two parts …. (Yes/no)

Content of Bidding Documents:

The materials / equipment required, bidding procedures, and contract terms are prescribed in the bidding documents as listed below:

        - Notice Inviting Bids.

        - Salient feature of the contract.

        - Standard General terms and conditions of contract.

        - Standard Technical specification and drawings wherever necessary.

        - Qualification Requirements.

        - Schedule of requirements (delivery Schedule)

SAMPLE FORMS.

        - Bid Form

        - Performance Security Form

i.		Manufacturers’ Authorization form

j. 	Performance Statement

k.	Details to be furnished by the Manufacturer (Format-A)

l.	Schedule of Deviations (Technical & Commercial)

The Bidder is expected to examine all instructions, forms, terms and technical specifications in the bidding documents. Failure to furnish all information required by the bidding documents or to submit a bid not substantially responsive to the bidding documents in every respect will be at Bidder's risk and may result in the rejection of its bid.

Deviations from standard bidding document

i)	General terms and Condition of Contract

ii)	Technical

The above deviations supercede the existing terms of GCC and Technical Specification

Chief general manager (P&MM)

TSSPDCL

SECTION - III

GENERAL TERMS AND CONDITIONS OF CONTRACT

A. Introduction

- Definitions

In this Contract, the following terms will be interpreted as indicated:

- "The Contract" means the agreement entered into between the Purchaser and the Supplier, as recorded in the contract Form signed by the Parties, including all attachments and appendices thereto and all documents incorporated by reference therein.

- "The Contract Price" means the price payable to the Supplier under the Contract for the full and proper performance of its contractual obligations.

(c)	"The Materials / equipment" means all of the equipment, machinery, and/or other materials which the Supplier is required to supply to the Purchaser under the Contract.

(d)	"The Services" means those services ancillary to the supply of the Materials / equipment, such as transportation and insurance, and any other incidental Services, such as installation, commissioning, provision of technical assistance, training, and other such obligations of the Supplier covered under the Contract.

(e)	"GCC" means the General Terms and Conditions of Contract contained in the section.

- "The Purchaser" means the organization purchasing the Materials / equipment.

- Vendor is a supplier who has registered with the purchaser for supply of materials/equipment.

(h)	"The Supplier" means the firm supplying the Materials / equipment and Services under this Contract.

(i)	"Day" means calendar day.

2.	Applicability

These General Conditions of contract will apply to the extent that they are not superseded by provisions of Salient features of the Bid.

3(a)	Standards

The Materials / equipment supplied under this Contract will conform to the Standards mentioned in the Technical specifications, and, when no applicable standard is mentioned, the authoritative standards appropriate to the Materials / equipment' i.e., BIS, such standards will be the latest. All material will be of the best class and will be capable of satisfactory operation under tropical conditions without distortion or deterioration.

3(b)	Interchangeability:

All similar materials and removable parts of similar equipment will be interchangeable with each other.  A specific confirmation of this should be furnished in the bid.

4. 	Scope of Work:

This specification covers design manufacture, testing and delivery FADS (Free At Destination Stores) of the materials described at Section V and Technical Specification Section VI.

5.	Eligible Bidders:

All the Manufacturers who have registered themselves with department of industries of State/Central Govt. with full manufacturing and testing facilities for supply of the material / equipment listed in Section No. V, of Bid specification and meeting the qualification requirements described at section IV and having BIS certification for the items quoted only need quote. Bids received from firms not meeting the above criteria will not be considered.

- THE BIDDING DOCUMENTS

6.	Contents of Bidding Document:

6.1	The Materials / equipment required, bidding procedures, and contract terms are prescribed in the bidding documents as listed below:

- Notice Inviting Bid

- Technical Specifications

- Schedule of Requirements (Delivery Schedule)

- Bid Form and Price Schedules(online only)

- Salient Features of the Bid

- General Terms and Conditions of Contract

- Qualification Requirements

- Bid Security

- Performance Security Form

- Schedule of Deviations

6.2	The Bidder is expected to examine all instructions, forms, terms and Technical specifications in the bidding documents. Failure to furnish all information required by the bidding documents or to submit a bid not responsive to the bidding documents in every respect will be at Bidder's risk and may result in the rejection of its bid.

7.	Clarification of Bidding Documents

Clarification of Bidding Documents: 	A prospective Bidder requiring any clarification of the bidding documents may notify the Purchaser in writing or by cable (hereinafter, the term cable is deemed to include telex and facsimile) at the Purchaser's address. The Purchaser will respond in writing to any request for clarification of the bidding documents, which it receives no later than fifteen (15) days prior to the deadline for the submission of bids. Written copies of Purchaser's response (including an explanation of the query but without identifying the source of inquiry) will be put on Website of the purchaser and e-procurement website or intimated by mail.

8.	Amendment to Bidding Documents:

8.1	At any time prior to the deadline for submission of bids, the Purchaser, for any reason, whether at its own initiative or in response to a clarification requested by a prospective Bidder, may modify the bidding documents by amendment.

8.2	All such amendments also would be made available on the website of TSSPDCL and                e-procurement website and such amendments will be binding on the respective Bidders.

8.3	In order to allow prospective Bidders reasonable time in which to take the amendment into account in preparing their bids, the Purchaser, at its discretion, may extend the deadline for the submission of bids.

### C. PREPARATION OF BIDS

9.	Language of Bid:

The bid prepared by the Bidder including all correspondence and documents relating to the bid exchanged by the Bidder and the Purchaser, will be in English.

10.	Cost Associated with Bidding:

The Bidder will bear all costs associated with the preparation and submission of its bid, and the Purchaser, will in no case be responsible or liable for those costs, regardless of the conduct or outcome of the bidding process.

11.	Documents Constituting the Bid:

The bid prepared by the Bidder will comprise the following components:

    - Bid Security in accordance with Clause No.19.

    - A Bid Form and Price Schedule (only for online submission) completed in accordance with Clause No.12 and 13.

    - Documentary evidence establishing in accordance with Clause No.18 that the Bidder is eligible to bid and is qualified to perform the contract if its bid is accepted.

    - Documentary evidence establishing that the Materials / equipment and ancillary services to be supplied by the Bidder are as per the Technical specification of the bidding documents; and

    - Tax clearance certificate

    - Schedule of Deviations

(a) Commercial

(b) Technical

All the Schedules will be duly filled but not necessary in the sheets attached to the specification unless full details required in the schedules are furnished the Bids will be liable for rejection.

12.	Bid Form:

The Bidder will complete the Bid form and the appropriate Price Schedule (only for online submission) furnished in the bidding documents, indicating the Materials / equipment to be supplied, a brief description of the Materials / equipment, quantity and prices.

13. 	Bid Prices:

13.1	The prices quoted shall be FIRM. Bids will be called for with prices FADS inclusive of packing and forwarding GST and other legally permissible duties and levies wherever applicable, handling charges to cover the transport by road from destination railway station to site/stores and insurance (transit and storage at site for 45 days).

13.2	Even though composite price is given the break-up for all the duties, taxes, freight, insurance, packing and forwarding etc., shall be furnished.

13.3	It is the responsibility of the Bidder to inform himself of the correct rates of duties and taxes leviable on the materials at the time of bidding.

13.4	The proforma credit available to the bidder on the purchases of inputs (raw materials) consequent to the introduction of “MODVAT” Scheme may be taken into account while quoting the prices.

13.5	The Bidder shall indicate on the appropriate Price Schedule (online submission) the unit prices (where applicable) and total bid price of the Materials / equipment it proposes to supply under the contract.

Prices indicated on the price schedule (online) shall be entered separately in the following manner.

The price of the Materials / equipment quoted EXWORKS and all excise and other duties and sales and other taxes payable on the finished Materials / equipment with individual breakup for Taxes and Duties, packing and forwarding, freight and insurance etc.

14.     Taxes and Duties

14.1   	A bidder will be entirely responsible for quoting the correct taxes and duties, other local taxes or levies if any, license fees, etc., he has to incur until completion of the contract. For the purpose of evaluation the bidder should clearly indicate the GST and any other levies payable. Failure to furnish such details leads to loading as indicated in the evaluation criteria.

14.2	If the rates of statutory levies assumed by the Bidder are less than the actual rates prevailing at the time of bidding, the Purchaser will not be responsible for such errors.  If the rates of statutory levies assumed by the Bidder are later proved to be higher than the actual / correct rates prevailing at the time of bidding, the difference will be passed on to the credit of the Purchaser.

14.3.	Deemed Export Benefits: This is not applicable for local purchases with TSSPDCL funds.

15.     	Statutory Variations

In case of subvendor items Taxes, Duties are inclusive in tender price. No statutory variation is applicable. Further price variations in respect of Sub-vendor items will be considered on tender prices.

Any variation up or down in statutory levy or new levies introduced after signing of the contract under this specification will be to the account of TSSPDCL provided. In cases where delivery schedule is not adhered to by the supplier and there are upward variation / revision after the agreed delivered date, the supplier will bear the impact of such levies and if there is downward variation / revision the TSSPDCL will be given credit to that extent. This is allowed only once during delivery period i.e. at the time of delivery of goods at factory.

16. 	Bid Currencies:

Prices shall be quoted in Indian Rupees; and will be paid in Indian Rupees Only.

17.	Quantity to quote:

Bidder shall quote a minimum quantity of at least 20% of the total quantity indicated in the bid Specification. Offers less than the minimum prescribed are liable for rejection.

18.	Documents Establishing Bidder’s Eligibility and Qualifications

The Bidder shall furnish, as part of its bid, documents establishing the Bidder's eligibility to bid and its qualifications to perform the contract if its bid is accepted.

The documentary evidence of the Bidder's qualifications to perform the contract if its bid is accepted will establish to the Purchaser's satisfaction:

(a)   That the Bidder has the financial, technical, and production capability necessary to perform the contract;

(b)	That the Bidder meets the qualification criteria listed in Section VI.  In addition the Bidder may furnish full particulars regarding supply of the material in question made so far to TSSPDCL during the last 5 years and other reputed utilities.

18.1 	Documents Establishing Materials/equipment Conformity to Bidding Documents.

The Bidder shall furnish as part of its bid, documents establishing conformity to the bidding documents of all Materials / equipment and services, which the Bidder proposes to supply under the Contract.

The documentary evidence of conformity of the Materials / equipment and the services to bidding documents may be in the form of literature, drawings, and data, and will consist of:

(a) a detailed description of the essential technical and performance characteristics of the Materials / equipment;

(b)	The bidder should specifically mention about furnishing the test certificates and a specimen form of test certificate should be furnished along with the bid.

(c)	a list giving full particulars, including available sources and current prices of spare parts,  special tools etc., necessary for the proper and continuing functioning  of the Materials / equipment following commencement of the use of the Materials / equipment by the Purchaser; and

(d)	an item-by-item commentary on the Purchaser's Technical Specifications demonstrating substantial responsive-ness of the Materials / equipment and services to those specifications, or a statement of deviations and exceptions to the provisions of the Technical Specifications.

For purposes of the commentary to be furnished pursuant to above, the Bidder will note that standards for workmanship, material, and equipment, as well as references to brand names or catalogue numbers designated by the Purchaser in its Technical Specifications, are intended to be descriptive only and not restrictive. The Bidder may substitute alternative standards, brand names, and/or catalogue numbers in its bid, provided that it demonstrates to the Purchaser's satisfaction that the substitutions ensure substantial equivalence to those designated in the Technical Specifications.

19.	Bid Security

19.1	The Bidder shall furnish, as part of its bid, a Bid Security in the amount of 2% of the Total Ex-works value of the materials offered against the bid (plus with GST @18%).  This amount should be paid by way of a crossed demand draft drawn on any schedule bank in favour of the Pay Officer, TSSPDCL and payable at headquarters of the Purchaser. The crossed DD should invariably be furnished along with the bids.  Alternatively the bidders may furnish a B.G. in original in lieu of DD as per the proforma attached. Fax / photocopies of the bid security will not be accepted and will be rejected.

19.2	The fact of having enclosed bid security by DD/B.G. along with the bid should be clearly super scribed on the bid envelope. Bids, which do not have the above superscription, will be rejected and returned to the respective bidders unopened.

19.3	Submission of BID SECURITY by way of Cheque, cash, money order, call deposit will not be accepted and will be considered as disqualification.

19.4	Payment of BID SECURITY will be waived at the discretion of the TSSPDCL in the case of fully owned Government undertaking of the Central or State Government.  Such undertakings should immediately apply and obtain exemption before submitting their Bids. They need only refer to the details of such exemption in their Bids. Exemption accorded by any organization other than TSSPDCL will not be considered.

19.5	Requests for exemption from payment of BID SECURITY will not be entertained in any other case.

19.6	Any bid not secured as above will be rejected by the purchaser.

19.7	Unsuccessful Bidders' Bid Security will be discharged or returned as promptly as possible, but not later than thirty (30) days after the expiry of the period of bid validity prescribed by the Purchaser.

19.8	The successful Bidder's Bid Security will be discharged upon the Bidder signing the contract.

19.9		The Bid Security may be forfeited:

(a)	if a Bidder:

    - Withdraws its bid or alters its prices during the period of bid validity specified by the Bidder on the Bid Form, or

    - Does not accept the correction of errors pursuant to Clause No.30.2; or

    - Offers post Bid rebates, revisions or deviations in quoted prices and / or conditions or any such offers which will give a benefit to the Bidder over others will not only be rejected outright but the original Bid itself will get disqualified on this account and the Bidder’s BID SECURITY will be forfeited.

(b)	In the case of a successful Bidder, if the Bidder fails:

    - To sign the contract in accordance with Clause No.37.

    - To furnish performance security in accordance with Clause No.38.

19.10	In cases where the Bid Cover Contains superscription of having furnished Bid Security by way of DD but if the same is not found within, such Bids will be rejected and bidder will run the risk of being banned.

Note : 	The bidder shall furnish required Bid Security amount and validity (The validity of the bank guarantee shall be upto bid validity +45 days from the date of tender opening ) as per specification.  If the bidder fails to furnish bid security amount and bid validity as stipulated in the specification, such tender bid will not be considered for further evaluation.

20.		Period of Validity of Bids.

20.1	Bids shall remain valid for the period of Ninety  (90) days from the date of bid opening prescribed by the Purchaser. A bid valid for a shorter period will be rejected.

The bidders should clearly super scribe on the sealed envelopes of the bids about the validity. Bids not containing superscription of validity will be rejected and returned unopened.

20.2	In exceptional circumstances, the Purchaser may solicit the Bidder's consent to an extension of the period of validity. The request and the responses there to will be made in writing (or by cable).  The Bid Security provided under Clause No.19 will also be suitably extended. A Bidder may refuse the request without forfeiting its Bid Security.

21. 	Tax Clearance Certificates:

Copies of Income Tax, Sales Tax and Turnover Tax certificates for the latest period from the appropriate authority will invariably be enclosed to the bid.  In the case of proprietary or partnership firm it will be necessary to produce the certificate / certificates for the proprietor or proprietors and for each of the partners as the case may be.  If the Bidder has already produced the certificate during the calendar year in which the bid is made, it will be sufficient, if particulars are given.

22.	Service Conditions

22.1	The equipment / materials offered will be entirely satisfactory for operation under the climatic conditions indicated below:

(a)	Maximum ambient air temperature (in shade)		450   C

(b)	Maximum ambient air temperature (under sun)		500   C

(c)	Maximum daily average ambient air temperature		350   C

(d)	Maximum yearly average ambient air temperature 		300   C

(e)	Maximum humidity 						100%

(f)	Altitude above M.S.L.						Up to 1000M

(g)	Average No. of thunder storm days per annum		50

(h)	Average No. of dust storm days per annum	             		Occasional

(i)	Average No. of rainy days / annum				90

(j)	Average Annual Rain fall 					925mm

(k)	Normal tropical monsoon period				4 months

(l)	Maximum wind pressure					150 kg/Sq.M.

22.2	Due consideration will be given to any special devices or attachments put forward by the Bidder which are calculated to enhance the general utility and the safe and efficient operation of the equipment / materials.

23.       Format and Signing of Bid.

23.1	The Bidder shall seal the original bid, duly marking envelope as "ORIGINAL". The envelopes will then be sealed in an outer envelope.

23.2	The original and the copies of the bid shall be typed and shall be signed by the Bidder or a person or persons duly authorized to bind the Bidder to the contract.  The person or persons signing the bid will initial all pages of the bid, except for printed literature.

23.3   	Any interlineations, erasures, or overwriting will be valid only if they are initialed by the person or persons signing the bid.

###### D. Submission of Bids

24.      Submission, Sealing and Marking of Bids.

  - The tenderers are required to submit their bids in two parts as under:

(i)	Part-I	:	Bid Security, Technical Bid & Qualification Requirements. Technical Bid shall contain full technical    particulars and commercial terms and conditions but without prices. This should not contain any cost information whatsoever.

Part-II 	:	Price Bid – containing Prices (shall be on-line only)

Bids received with any details pertaining to prices in the offline mode will be liable for rejection.

(ii)	The Part-I of tender should be furnished in a sealed cover super scribing tender enquiry number, name of material, name of the bidder and date of tender opening

(iii)	Part-I of the bid will be opened on the due date of tender opening.  In case the bidders have been granted Bid Security exemption (clause-19), documentary evidence for the same must be furnished.  The firms whose Bid Security, Testing charges and Transaction Fee are not received as specified in the tender document, the price bids will not be opened and their bids will be rejected summarily.

(iv)	The price bids of only those bidders whose technical bids, on examination, are determined to be technically and commercially acceptable and meeting the specified Qualification Criteria will be opened at a later date.

Sealing and Marking of Bids.

24.2  	The Bidder shall seal the bid in an envelope.

24.3    The inner and outer envelopes will be  addressed to the purchaser.

24.4    The sealed cover as well as the outer envelope should be super scribed as follows:

- Bid Enquiry No.

- Due date and time for hard copy and online submission.

- Date and time for online opening.

- Payment of Bid Security

(i)     If paid, give details: D.D. No……. Date: ……..

- Whether 90days validity offered……….YES / NO

- Payment of testing charges D.D. No……. Date: ……..

- Whether the quotation is made accepting Payment terms clause …. YES/NO

- Whether the delivery is as per delivery schedule indicated…. YES/NO

- Whether the sample (if specified) has been enclosed/ sent…YES/NO

- Whether the bid is quoted in two parts (clause 24.1)…. (YES/NO)

  - Bids not super scribed as above are liable to be rejected.

24.6 	The Bidder shall invariably complete the Bid in full. Details to be furnished by the bidder and Schedule of Prices attached to the specification and enclose the same to the bid without fail.

24.7	The bids shall be in bound volumes (With the documents in the volume not detachable). All pages of the bid except in-amended printed literature shall be initiated by the person/persons signing the bid. The page number shall be referred in Index. All pages including literature, type test reports of the bid shall be numbered and the page numbers shall be continuous. Soft copy of the technical and commercial bids and designs with drawings shall be given in Floppy disc/ CD also. Summary sheet in the given format on the top of the bid duly signed and sealed by the bidder.

24.8	The time of actual receipt in the office only will count for the acceptance of the bid and either the date of bid, date stamp of post office or date stamp of any other office will not count. The TSSPDCL will not be responsible for any postal or any other transit delays.

24.9	Telegraphic quotations will not be entertained under any circumstances. Clarification, amplifications, and/or any other correspondence from the Bidder subsequent to the opening of bid will not be entertained.  The Bidders are advised to ensure that their bids are sent in complete shape at the first instance itself.

24.10	The inner envelopes shall also indicate the name and address of the Bidder to enable the bid to be returned unopened in case it is declared "late".

24.11	If the outer envelope is not sealed and marked as required above, the Purchaser will assume no responsibility for the bid's misplacement or premature opening.

25. 	Deadline for Submission of Bids.

25.1	Bids together with modifications if any, or other withdrawals must be received by the Purchaser not later than the deadline for submission of bids specified in the Salient features of the Bid.

25.2	The Purchaser may, at its discretion, extend this deadline for the submission of bids by amending the bidding documents in which case all rights and obligations of the Purchaser and Bidders previously subject to the deadline will thereafter be subject to the deadline as extended.

26.       Late Bids

26.1	Any bid received by the Purchaser after the deadline for submission of bids prescribed by the Purchaser will be rejected and returned unopened to the Bidder.

26.2     Modification and Withdrawal of Bids.

The Bidder may modify or withdraw its bid after the bid's submission, provided that written notice of the modification, including substitution or withdrawal of the bids, is received by the Purchaser prior to the deadline prescribed for submission of bids.

The Bidder's modification or withdrawal notice will be prepared, sealed, marked, and dispatched. A withdrawal notice may also be sent by cable, but followed by a signed confirmation copy, postmarked not later than the deadline for submission of bids. No bid may be modified after the deadline for submission of bids.

No bid may be withdrawn in the interval between the deadline for submission of bids and the expiration of the period of bid validity specified. Withdrawal of a bid during this interval may result in the forfeiture of its Bid Security.

###### E. 	Opening and Evaluation of Bids

27.       Opening of Bids by the Purchaser

27.1	The Purchaser will open all bids meeting above criteria at the time, on the date, and at the place specified.

27.2   	The Bidders' names, bid modifications or withdrawals, discounts and the presence or absence of requisite Bid Security and such other details as the Purchaser, at its discretion, may consider appropriate, will be announced at the opening.

27.3  	Bids that are not opened at bid opening will not be considered further for evaluation, irrespective of the circumstances.

28.	     Clarification of Bids

During evaluation of the bids, the Purchaser may, at its discretion, ask the Bidder for a clarification of its, bid.  The request for clarification and the response shall be in writing, and no change in the prices or substance of the bid shall be sought, offered, or permitted.

29.	    Preliminary Examination

29.1	The Purchaser will examine the bids to determine whether they are complete, whether any computational errors have been made, whether required sureties have been furnished, whether the documents have been properly signed, and whether the bids are generally in order.

29.2 	Arithmetical errors will be rectified on the following basis. If there is a discrepancy between the unit price and the total price that is obtained by multiplying the unit price and quantity, the unit price will prevail, and the total price will be corrected.  If the Supplier does not accept the correction of the errors, its bid will be rejected, and its Bid Security may be forfeited.  If there is a discrepancy between words and figures, the amount in words will prevail.  If the supplier does not accept the correction of the errors, its bid will be rejected and its Bid Security may be forfeited.

29.3 	The Purchaser may waive any minor informality, nonconformity, or irregularity in bid which does not constitute a material deviation, provided such waiver doesn't prejudice or affect the relative ranking of any Bidder.

29.4  	Prior to the detailed evaluation, the Purchaser will determine the substantial responsiveness of each bid to the bidding documents.  For purposes of these Clauses, a substantially responsive bid is one, which conforms to all the terms and conditions of the bidding documents without material deviations. Deviations from, or objections or reservations to critical provisions, such as those concerning Bid Security, and Taxes and Duties will be deemed to be a material deviation.  The Purchaser's determination of a bid's responsiveness is to be based on the contents of the bid itself without recourse to extrinsic evidence.

29.5  	If a bid is not substantially responsive, it will be rejected by the Purchaser and may not subsequently be made responsive by the Bidder by correction of the nonconformity.

Note :		Payment terms, Delivery period, Performance Bank Guarantee, Taxes and Duties” 	should be in line with the terms and conditions of the specification. If any bidder 	does not meet any one of the conditions, such tender will not be considered. Please 	note that the conditional offers are also not considered. Hence the bidder shall 	submit the tender in line with the terms and conditions of the specification.

30.	Evaluation and Comparison of Bids.

30.1	The Purchaser will evaluate and compare the bids, which have been determined to be substantially responsive.

30.2	The Purchaser's evaluation of a bid will take into consideration one or more of the following factors

All the bids, which are opened, read out and considered for evaluation, will be checked for qualification requirements in respect of technical and commercial aspects. Such of the bids, which do not meet the qualification requirements, will not be evaluated further. The bid is to be checked for its conformity to the technical specification. If it does not meet the technical specification, the Bid will not be evaluated further. However, if in the opinion of the purchaser the bidder has offered equipment / material better than the technical specification the same may be considered. The bid may be rejected for the following reasons:

1.   Not in the prescribed form

- Insufficient bid security or bid not accompanied by the required bid security or proof of exemption.

- Bids not properly signed

- The bidder is a vendor who is banned from further business transactions and the period of ban is still in force.

- Bid received after the due date and time

- The bid is through telegram or fax

- Further, the purchaser may enquire from the bidder in writing for any clarification of the bid. The response of the bidder will also be in writing. However no change in the prices or substance of the bid will be sought, offered or permitted.

- Bids will be examined for completeness and for any computational errors.

- Arithmetical errors will be rectified on the following basis.

  - Where there is a discrepancy between the unit price and total price, the unit price will prevail and the total price will be corrected accordingly.

  - Where there is a discrepancy between words and figures, the amount in words will prevail.

  - Failure on the part of the bidder to agree to the above corrections will result in rejection of his offer and forfeiture of his bid security.

- It will be ensured that the required sureties have been furnished and that the documents have been properly signed.

- The purchaser's evaluation of a bid will take into consideration one or more of the following factors

(a)	Delivery schedule offered in the bid;

(b)	Deviations in payment schedule from that specified in the general terms and conditions of the contract and technical deviations.

(c)	The cost of components, mandatory spare parts, and service;

(d)	The availability of spare parts and after-sales services for the equipment offered in the Bid;

(e)	The projected operating and maintenance costs during the life of the equipment;

(f)	The performance and productivity of the equipment offered;

(g)	Other specific criteria indicated in the Bidding documents.

In addition the Purchaser’s evaluation of a bid will take into account the net landed cost of the material at the final destination. For the purpose of evaluation net landed cost is arrived at by adding all elements of the basic price, allowable discount, excise duty & any other levies, packing & forwarding, freight charges, insurance (transit & storage) as quoted by the bidder, interest on advance if any, erection, servicing  other charges and inclusive of GST  as called for.

In addition any variation up or down in taxes and duties / new levies introduced subsequent to bid opening and before award will be considered for comparison purposes.

The following criteria may be adopted for taxes and duties for evaluation

a.     It is the responsibility of the bidder to quote all taxes and duties correctly without leaving any column unfilled. Where taxes and duties are not applicable the bidder should enter “NA”.  If no duty / tax is le-viable the same may be entered as “NIL”. If any column is left blank or filled vaguely like “as applicable”, the same will be loaded with the maximum of the other eligible Bids.

  - Where there is an exemption of GST, the documentary evidence to that effect will be enclosed by the supplier.

c.	The bidders for supply and works shall invariably possess the GSTIN number and PAN Number for the bids above Rs. 5.00 lakhs and this must be verified before entering into contract.

- Prior to detailed evaluation, the responsiveness of each bid will be determined. A substantially responsive bid is one that conforms to all the terms and conditions of the bidding documents without material deviations. For this purpose superscription, qualification requirement, bid security, validity, delivery, payment term, price schedule, taxes and duties will be deemed to be the critical provisions and deviations in any one of these items will be deemed to be a material deviation.

The purchaser may waive any minor informality, non-conformity or irregularity in the bid which does not constitute a material deviation, provided such waiver does not affect the relative ranking of any bidder.  The purchaser will clearly indicate in the bid specification the methodology for evaluation of bids.

(a)	Bid price, which will include all, costs of manufacture and services at manufacturing place as well as, Transportation to destination stores, packing and forwarding, insurance and all Taxes & other legally permissible duties& levies payable.

(b)	Delivery schedule offered in the bid.

(c)	Deviations in payment schedule from that specified in the general terms and conditions of the contract.

(d)	The cost of components, mandatory spare parts, and service

(e)	The availability of spare parts and after-sales services for the equipment offered in the Bid;

(f)	The projected operating and maintenance costs during the life of the equipment;

(g)	The performance and productivity of the equipment offered; and/or

- Other specific criteria indicated in the Bid Specification.

30.3(a) The Purchaser’s evaluation of a bid will take into account the Net Landed Cost of the Material at destination stores inclusive of all taxes and duties and inclusive of GST quoted by the Bidder.  It is the responsibility of the bidder to quote all Taxes and Duties correctly without leaving any column unfilled.  Where not applicable the column may be filled as “NA”.  If no duty / tax is le-viable the same may be filled as “NIL”. If any column is left blank the same is loaded with maximum of other eligible Bids.

30.3(b) Any statutory variations of taxes and duties and new levies imposed after opening of the bid and before award of the contract will be taken into consideration for the purpose of evaluation.

30.4	A substantially responsive bid is one, which conforms to all the terms and conditions of the bidding documents without material deviations. For this purpose superscription, qualification requirement, bid security, validity, delivery, payment term, price schedule, submission of Types test certificates (as per Clause 4 section VI), taxes and duties will be deemed to the critical provisions and deviations in any one of these things will be deemed to be a material deviation.

31.	Contacting the Purchaser.

31.1	From the time of the bid opening to the time of contract award, if any Bidder wishes to contact the Purchaser on any matter related to the bid, it should do so in writing.

31.2	Any effort by a Bidder to influence the Purchaser in its decisions on bid evaluation, bid comparison, or contract award will result in the rejection of the Bidder's bid.

F. 	Award of Contract.

32.       Post Qualification

32.1	In the absence of pre-qualification, the Purchaser will determine to its satisfaction whether the Bidder that is selected as having submitted the lowest evaluated responsive bid is qualified to perform the contract satisfactorily.

32.2  	The determination will take into account the Bidder's financial, and production capabilities.  It will be based upon an examination of the documentary evidence of the Bidder's qualification submitted by the Bidder, as well as such other information as the Purchaser deems necessary and appropriate.

33.	Award Criteria:

The Purchaser will award the contract to the successful Bidder / Bidders whose bid has / have been determined to be substantially responsive.

However it is not binding on TSSPDCL to accept the lowest or any other Bid.  It reserves the right to place orders on different Bidders.

34.	Purchaser’s Right to Vary Quantities at Time of Award

34.1	The Purchaser reserves the right at the time of contract award to increase or decrease the quantity by +/- 50%of Materials / equipment and services originally specified in the Schedule of Requirements without any change in unit price or other terms and conditions.

34.2	The purchaser reserves the right to vary the ordered quantity by +/- 50% during the execution of the contract.

35.	Purchaser's Right to Accept Any Bid and to Reject Any or All Bids

The Purchaser reserves the right to accept or reject any bid, and to annul the bidding process and reject all bids at any time prior to contract award, without thereby incurring any liability to the affected Bidder or Bidders or any obligation to inform the affected bidder or bidders.

36.	Notification of Award

36.1	Prior to the expiration of the period of bid validity, the Purchaser will notify the Successful Bidder in writing by registered letter or by cable, to be confirmed in writing by registered letter, that its bid has been accepted.

36.2	The notification of award will constitute the formation of the Contract.

36.3  	Upon the successful Bidder's furnishing of the performance security, the Purchaser enters into contract with successful Bidder / Bidders. The Purchaser will notify each unsuccessful Bidder and will discharge its Bid Security.

37.	Signing of Contract:

The Purchaser notifies the successful Bidder that its bid has been accepted.

Within 30 (thirty days) of receipt of notification of award of Contract, the successful Bidder will sign and date the contract. Failure to comply with this stipulation will entail cancellation of the contract besides forfeiture of the bid security.

38.	Performance Security:

38.1   	Within Fifteen (15) days of receipt of the notification of Contract award. The successful Bidder will furnish to the Purchaser the performance security for an amount 10% of the contract value for proper fulfillment of the contract, which will include the warranty period, and completion of performance obligations including Warranty obligations. The Performance Security will cover 60 days beyond the date of completion of performance obligations including Warranty obligations.

In the event of any correction of defects or replacement of defective material during the warranty period, the warranty for the corrected / replaced material will be extended to a further period of 12 months and the Performance Bank Guarantee for proportionate value will be extended 60 days over and above the extended warranty period.

38.2  	 The proceeds of the performance security will be payable to the Purchaser as compensation for any loss resulting from the Supplier's failure to complete its obligations under the Contract.

38.3 	The performance security will be…

- A bank guarantee issued by a Nationalized bank or scheduled bank acceptable to the Purchaser, in the form provided in the bidding documents.

- A banker's cheque or crossed DD or Pay Order payable at the Head quarter of    the Purchaser in favour of the Purchaser drawn on any scheduled bank.

38.4   	The performance security will be discharged by the Purchaser and returned to the Supplier not later than sixty (60) days after the expiry date.

38.5   Failure of the successful Bidder to comply with the above requirement will entail cancellation of the award and forfeiture of the Bid Security and the balance to make up the performance security deposit will be deducted form pending payments if any due to the tenderer form TSSPDCL on other orders in addition the company will also become liable for being black listed by TSSPDCL.

39.	Corrupt or Fraudulent Practices

It is essential that the Purchaser as well as Bidder/supplier / contractor for the purposes of this provision, the terms set forth below as follows:

(i) “Corrupt practice” means the offering, giving, receiving or soliciting of any thing of value to influence the action of a public official in the procurement process or in contract execution, and

(ii) “Fraudulent practice” means a misrepresentation of facts in order to influence a procurement process or the execution of a contract to the determinant of the purchaser, and includes collusive practice among Bidders (prior to or after bid submission) designed to establish bid prices at artificial non-competitive levels and to deprive the purchaser of the benefits of free and open competition;

(iii) Will reject a proposal for award if it determines that the Bidder recommended for award has engaged in corrupt or fraudulent practices in competing for the contract in question;

(iv) Will declare a firm ineligible, either indefinitely or for a stated period of time, to be awarded a contract if it at anytime determines that the firm has engaged in corrupt or fraudulent practices in competing for, or in executing, a contract.

40.	Use of Contract Documents and Information:

40.1	The Supplier will not, without the Purchaser's prior written consent, disclose the Contract, or any provision thereof, of any specification, plan, drawing, pattern, sample, or information furnished by or on behalf of the Purchaser in connection therewith, to any person other than a person employed by the Supplier in the performance of the Contract.  Disclosure to any such employed person will be made in confidence and will extend only so far as may be necessary for purposes of such performance.

40.2	The Supplier will not, without the Purchaser's prior written consent, make use of any document or information except for purposes of performing the Contract.

40.3	Any document, other than the Contract itself, will remain the property of the Purchaser and will be returned (in all copies) to the Purchaser on completion of the supplier's performance under the Contract if so required by the Purchaser.

40.4   	The Supplier will permit the Purchaser or his authorized representative to inspect the Supplier’s accounts and records relating to the performance of the Supplier and to have them audited by auditors appointed by the Supplier.

41.	Patent Rights

The Supplier will indemnify the Purchaser against all third-party claims of infringement of patent, trademark, or industrial design rights arising from use of the Materials / equipment or any part thereof.

42.	Places / Locations:

Particulars of site location and nearest rail heads to which the equipments / material have to be supplied will be given to successful Bidders.

43.	Delivery:

Delivery period will be reckoned from the date of signing of the contract.  The delivery quoted will be firm, definite, unconditional and on the basis of receipt of materials at destination in good condition without any bearing on the procurement of raw materials or any similar prerequisites.  The commencement date and date of delivery will be indicted. The preferred delivery time, which is the essence of this specification, is indicated in the schedule.  Final deliveries are however, subject to confirmation at the time of Contract.  Delay in delivery of materials FADS – (Free At Destination Store) due to non-availability of railway booking, non-allotment of wagons and any such reasons will not be considered.  It is the responsibility of the supplier to make alternative arrangements for transporting the materials by road or rail so as to see that the material reaches the destination within the stipulated period.  The Purchaser reserves its right to defer the delivery date at any time after orders are placed without any change in the conclusion of contract other conditions supply.  The delivery period, which will be reckoned from the date of the Contract, will be guaranteed under penalty as in Clause 61.

44.     Inspections and Tests

(i)  The supplier will keep the Purchaser informed in advance of the time of the   starting and the progress of manufacture of equipment in its various stages so that arrangement could be made for inspection. The accredited representative of the TSSPDCL will have access to the supplier’s or his subcontractor’s work at any time during working hours for the purpose of inspecting the materials during manufacturing of the materials / equipment and testing and may select test samples from the materials going into plant and equipment.  The supplier will provide the facilities for testing such samples at any time including access to drawings and production data at no charge to Purchaser.  As soon as the materials are ready the supplier will duly send intimation to TSSPDCL by Regd. Post and carry out the tests in the presence of representative of the TSSPDCL.

(ii)	The TSSPDCL may at its option get the materials inspected by the third party if it feels necessary and all inspection charges in this connection will be borne by the TSSPDCL. In case of material, not of acceptable quality or not conforming to the specification, the materials will be rejected. The material has to be re-offered for inspection. In such a case the 2nd inspection charges are to suppliers account. In case the materials are rejected in the 2nd inspection also, the TSSPDCL reserves the right to cancel the order.

(iii)  The dispatches will be affected only if the test results comply with the specification.  The dispatches will be made only after the inspection by the TSSPDCL Officer is completed to the TSSPDCL satisfaction or such inspection is waived by the competent authority.

(iv)  The acceptance of any quantity of materials will in no way relieve the supplier of its responsibility for meeting all the requirements of this specification and will not prevent subsequent rejection if such materials are later found to be defective.

(v)  The supplier will give 15 days advance intimation to enable the Purchaser to depute his representative for witnessing the acceptance and routine tests.

(vi) 	Should any inspected or tested materials / equipment fail to conform to the specification, the Purchaser may reject the materials and supplier will either replace the rejected materials or make alterations necessary to meet specifications requirements free of costs to the Purchaser.

(vii) In the case of transformers, instrument transformers and meters inspection will be conducted every year, for the first 5 years on a 2% sample of the quantities supplied.  Samples will be collected at random to establish that the guaranteed technical parameters are as per the submitted bid by the supplier. In the case of non-adherence, the purchaser may take suitable action on the supplier including cancellation of vendor registration and banning further dealings, depending on the gravity of the deviation. These random inspections may be entrusted to a third party.

(viii) Inspection not carried out due to non-readiness of the material even after contacting / confirmed over phone from the supplier about availability of material    and physical verification at the supplier premises, the charges @ 0.3% of Ex-works price of material offered for inspection (inclusive of GST and all other taxes & duties, travelling expenses, boarding and lodging charges at the place of inspection and all incidental charges) shall be paid by supplier subject to a maximum of Rs. 10,000.00

45.	Name Plate:

Equipment should be provided with name plate giving full details of manufacture, capacities and other details as specified in the relevant ISS or other specification stipulated.  The contract No. and date and year of supply and the words “TSSPDCL” must be etched on the name plate.

46.	Packing

46.1	The Supplier will provide such packing of the Materials / equipment as is required to prevent their damage or deterioration during transit to their final destination, as indicated in the Contract. The packing will be sufficient to withstand, without limitation, rough handling during transit and exposure to extreme temperatures, salt and precipitation during transit, and open storage.  Packing case size and weights will take into consideration, where appropriate, the remoteness of the Materials / equipment' final destination and the absence of heavy handling facilities at all points in transit.

46.2   	The packing, marking, and documentation and outside the packages will comply strictly with such special requirements as will be expressly provided for in the Contract and in any subsequent instructions ordered by the Purchaser. The supplier will be required to make separate packages for each consignee; each package will be marked on three sides with proper paint / indelible ink with the following;

- Contract Number

  - Supplier’s name

  - Packing list reference number

46.3 The supplier, whenever dispatches material to a destination should prepare the following information in the form of packing slip in quadruplicate and send the same to the consignee and obtain his acknowledgement. The consignee will return to the supplier one copy of the packing slip with his remarks.  The proforma of packing slip will be as follows:

# PACKING SLIP

- Contract No. & Date.

- Quantity allotted to the stores and rate applicable.

- Quantity so far supplied to the stores and the rate applied.

- Quantity now supplied and the rate applied.

- Total quantity supplied under the Contract with rates applied.

- Programme for supplying the balance quantity to the Stores.

47.        Delivery Documents

47.1	Delivery of the Materials/equipment will be made by the Supplier in accordance with the terms specified in the contract.

The latest test certificates containing the result of the tests as per the relevant ISS or other specification stipulated must be submitted to the Chief General Manager (P&MM) and got approved by him.

47.2	Documents to be submitted by the Supplier are specified as under…

(i)  	Insurance certificate;

(ii)	Supplier’s certificate certifying that the defects if any pointed out during inspection has been rectified (3 copies).

(iii)	Manuals in Six sets and one set of reproducible drawings.

The Purchaser will receive the above documents soon after the dispatch of materials and if not received, the supplier will be responsible for any consequent expenses.

48.     Insurance

    - The Materials / equipment supplied under the Contract will be fully insured against loss or damage incidental to manufacture or acquisition, transportation and delivery and also storage for 45 days at destination stores before taking into account.

    - The bidder shall a) Initiate and pursue insurance claim till settlement, and b) Promptly arrange for repair and/or replacement of any damaged items in full irrespective of settlement of insurance claim by the under Writers. c) All costs because of insurance liabilities covered under the contract will be to supplier’s account. The supplier shall provide the Purchaser with a copy of all insurance policies and documents taken out  by him in pursuance of the ‘Contract’. Such copies of documents shall be submitted to the purchaser immediately after such insurance coverage. The supplier shall also inform the Purchaser in writing at least sixty (60) days in advance, regarding the expiry, cancellation and/or change in any of such documents and ensure revalidation/renewal etc., as may be necessary well in time.

The risks that are to be covered under the insurance shall be comprehensive and shall include but not limited to, the loss or damage in transit, storage, due to theft, pilferage, riot, civil commotion, weather conditions, accident of all kinds, fire, flood, war risk(during ocean transportation) bad or rough handling etc. The scope of such insurance shall cover the entire contract value.

The insurance will be in an amount equal to 100% FADS value of Materials / equipment on all risks basis. The policy will have a provision for extension to cover further storage if necessary at destination stores / site at TSSPDCL cost. The supplier will take the insurance cover in the name of purchaser.

49.	Transportation

The Supplier is required under the Contract to transport the Materials / equipment to a specified place of destination defined as normally the district stores, transport to such place of destination, including insurance and storage, will be arranged by the Supplier, and the related costs will be included in the Contract Price only.

50.       Incidental Services

The Supplier may be required to provide any or all of the following services, including additional services, if any.

(a)	Performance or supervision of on-site assembly and/or start-up of the supplied Materials / equipment;

(b)	Furnishing of tools required for assembly and/or maintenance of the supplied Materials / equipment;

(c)	Furnishing of a detailed operations and maintenance manual for each appropriate unit of the supplied Materials / equipment;

(d)	Performance or supervision or maintenance and/or repair of the supplied Materials / equipment, during warranty period, provided that this service will not relieve the Supplier of any warranty obligations under this contract; and

(e)	Training of the Purchaser's personnel, at the Suppliers' plant and/or on-site, in assembly, start-up, operation, maintenance, and/or repair of the supplied Materials / equipment.

51.  	Spare Parts

The Supplier may be required to provide any or all of the following materials, notifications, and information pertaining to spare parts manufactured or distributed by the Supplier.

        - Such spare parts as the Purchaser may choose to purchase from the Supplier, provided that this election will not relieve the supplier of any warranty obligations under the contract; and

        - In the event of termination of production of the spare parts:

        - Advance notification to the Purchaser of the impending termination.

        - Time to permit the Purchase to procure needed requirement; and following such termination, furnishing at no cost to the Purchaser, the blueprints, drawings, and specifications of the spare parts, if requested.

52.	Warranty

52.1	The supplier will warrant for the satisfactory functioning of the material / equipment as per specification for a minimum period of 5 years from the date of receipt of the material / equipment in good condition.

52.2	The Supplier warrants that the Materials/equipment supplied under the Contract are new, unused, of the most recent or current models and that they incorporate all recent improvements in design and materials unless provided otherwise in the Contract. The supplier further warrants that all Materials/equipment supplied under this Contract will have no defect, arising from a design and /or materials as required by the Purchaser's specifications or from any act of omission of the Supplier that may develop under normal use of the supplied Materials/equipment.

52.3	All the material will be of the best class and will be capable of satisfactory operation in the tropics under service conditions indicated in clause 23.1 without distortion or deterioration.  No welding filling or plugging of defective parts will be permitted, unless otherwise specified, they will conform to the requirements of the appropriate Indian, British or American Standards. (Where a standard specification covering the material in question has not been published, the standards of the American Society for testing of Materials should be followed).

52.4	The entire designs and construction will be capable of withstanding the severest stresses likely to occur in actual service and of resisting rough handling during transport.

52.5	Unless otherwise specified the warranty period will be 5 years from the date of acceptance of the Materials / equipment. The Supplier will, in addition, comply with the performance guarantees specified under the contract.  If, for reasons attributable to the Supplier, these guarantees are not attained in whole or in part, the supplier will at its discretion either, Make such changes, modifications, and/or additions to the Materials / equipment or any part thereof as may be necessary in order to attain the contractual guarantees specified in the contract at its own cost and expense and to carry out further performance tests as per the relevant standards.

52.6	The Purchaser will promptly notify the supplier in writing of any claims arising under this warranty.

52.7  	"Upon receipt of such notice, the Supplier will within 30 days repair or replace the defective Materials/equipment or parts thereof, free of cost at the ultimate destination.  The supplier will take over the replaced parts/Materials / equipment at the time of their replacement.  No claim whatsoever will lie on the Purchaser for the replaced parts/Materials/equipment thereafter". In the event of any correction of defects or replacement of defective material during the warranty period, the warranty for the corrected/replaced material will be extended to a further period of 12 months.

52.8    	If the Supplier, having been notified, fails to remedy the defect(s) within the above period, the Purchaser may proceed to take such remedial action as may be necessary, at the Supplier's risk and expense duly deducting the expenditure from subsequent bills / bank guarantee and without prejudice to any other rights which the Purchaser may have against the Supplier under the Contract.

53.	Payment

“100% payment will be arranged on or after 30 days from the date receipt of 	material/equipment at the destination/stores (i.e.103 entry in SAP module) duly 	transferring the said amount to the bank account of the supplier by the purchaser 	bank. The supplier will have to predefine the Bank details while entering into contract 	for electronic transfer of payments.

Note:

- The date of delivery would be the date on which the stores officer certifies the receipt of materials at stores in good condition 103 entry in SAP module in respective of the date of check measurement.

- Form 13 shall be issued subject to material taken into stock in good condition (i.e. 105 entry in SAP module)

- The supplier should invariably submit test certificates as soon as despatch is made so that the test certificates can be checked up and approved well before it becomes due for payment. Routine Test Certificates of the entire lot shall be submitted to the Consignee.

- The performance guarantee to be executed in accordance with this specification shall be furnished on a stamp value of Rs.100/- The performance guarantee shall be from any Nationalized/Scheduled Bank. Performance Guarantee to the extent of 10% value of purchase order valid upto 2 months over and above the guarantee period to draw 100% payment.

The performance guarantee has to be extended suitably by you in accordance with the guarantee clause, so that the last consignment against the order is covered by the guarantee.

- If you have received any over payments by mistake or if any amounts are due to the TSSPDCL due to any other reason, when it is not possible to recover such amounts under the contract resulting out of the subject specification, the TSSPDCL reserves the right to collect the same from any other amounts and/or bank guarantee given by you due to or with the TSSPDCL.

- When you do not at any time, fulfill your obligations in replacing / rectifying etc., of the damaged/ defective materials in part or whole promptly to the satisfaction of the TSSPDCL officers, the TSSPDCL reserves the right not to accept the bills against subsequent dispatches made by the supplier and only the supplier will be responsible for any demurrages, wharf ages or damages occurring to the consignment so dispatched.

54.     	Prices

Prices charged by the Supplier for Materials / equipment delivered and Services performed under the Contract will not vary from the prices quoted by the supplier in its bid, with the exception of any price adjustment authorized in the contract.

55.	Change Orders

The Purchaser may at any time, by a written order given to the Supplier make changes within the general scope of the Contract   in any one or more of the following:

- Drawings, designs, or specifications, where Materials / equipment to be furnished under the Contract are to be specifically manufactured for the Purchaser;

- The method of shipment or packing;

- The place of delivery; and/or

- The Services to be provided by the Supplier.

56.	Contract Amendments

No variation in or modification of the terms of the Contract will be made except by written amendment by the Purchaser and accepted by the supplier.

57.	Assignment

The Supplier will not assign, in whole or in part, its obligations to perform under this Contract, except with the Purchaser's prior written consent.

58.	Delays in Supplier’s Performance

58.1	Delivery of the Materials / equipment will be made by the Supplier in accordance with the time schedule prescribed by the Purchaser in the Schedule of Requirements.

58.2   	If at any time during performance of the Contract, the Supplier should encounter conditions impeding timely delivery of the Materials / equipment, the Supplier will promptly notify the Purchaser in writing of the fact of the delay, its likely duration and its cause(s). As soon as practicable after receipt of the Supplier's notice, the Purchaser will evaluate the situation and may at its discretion extend the Supplier's time for performance, with or without liquidated damages, in which case the extension will be ratified by the parties by amendment of the Contract.

58.3   	Except as provided under force measure clause a delay by the Supplier in the performance of its delivery obligations will render the Supplier liable to the imposition of liquidated damages unless an extension of time is agreed upon without the application of liquidated damages.

59.		Penalty for delay in supplies

The time for and the dates for delivery mentioned in the contract will be deemed to be the essence of the contract.  Subject to force measure Clause No.64, if the Supplier fails to deliver any or all of the Materials/equipment or to perform the Services within the period(s) specified in the Contract, the Purchaser will, without prejudice to its other remedies under the Contract, deduct from the Contract Price, as liquidated damages, a sum equivalent to 0.5% per week on the undelivered portion subject to a maximum of 5% of the cost of the undelivered portion within scheduled time. Once the maximum is reached the Purchaser may consider termination of the contract.

The check measurement date ie., the date of receipt of materials at destination stores in good condition will be taken as the date of delivery. For calculation of penalty the date of receipt of material at the destination stores is the date of delivery subject to the condition that the goods/material are received in good condition. Materials / Equipment which are not of acceptable quality or are not confirming to the specification would be deemed to be not delivered. For penalty, the number of days would be rounded off to the nearest week and penalty calculated accordingly.

The penalty specified above will be levied and would be adjusted against subsequent pending bills.

In cases where new vendors fail to meet the requirement of the Contract there would be no penalty to such vendors but they will be excluded from the next bid for the particular item of the material.

Any failure on the part of new vendors for a second time would cause them to be removed from the list of registered vendors.

60.    	Risk Purchase

Incase of supplier who has not adhered to the delivery schedule, the TSSPDCL reserves the right to purchase the balance quantity from the open market/floating another tender and recover the extra expenditure thus incurred from the supplier.

61	Termination for Default

61.1	The Purchaser, without prejudice to any other remedy for breach of Contract, by written notice of default sent to the Supplier, may terminate this Contract in whole or in part:

i. If the Supplier fails to deliver any or all of the Materials / equipment within the period(s) specified in   the Contract, or within any extension thereof granted by the Purchaser.

ii.   If the Supplier fails to perform any other obligation(s) under the Contract.

iii. If the Supplier, in the judgment of the Purchaser has engaged incorrupt or

Fraudulent practices in competing for or in executing the Contract.

61.2  	 In the event the Purchaser terminates the Contract in whole or in part, the Purchaser may procure, upon such terms and in such manner, as it deems appropriate, Materials / equipment or services similar to those undelivered, and the Supplier will be liable to the Purchaser for any excess costs for such similar Materials / equipment or Services.  However, the Supplier will continue performance of the Contract to the extent not terminated.

62.	Termination for Insolvency

The Purchaser may at any time terminate the Contract by giving written notice to the Supplier if the Supplier becomes bankrupt or otherwise insolvent. In this event, termination will be without compensation to the supplier, provided that such termination will not prejudice or not affect any right of action or remedy, which has accrued or will accrue thereafter to the Purchaser.

63.	Termination for Convenience

63.1   	The Purchaser, by written notice sent to the Supplier, may terminate the Contract, in whole or in part, at any time for its convenience. The notice of termination will specify the termination is for the Purchaser's convenience, the extent to which performance of the supplier under the Contract is terminated, and date upon which termination becomes effective.

63.2 	However the Materials / equipment that are complete and ready for shipment within thirty (30) days after the supplier's receipt of notice of termination will be accepted by the Purchaser at the Contract terms and prices.

64.	Force Majeure

64.1	The Supplier will not be liable for forfeiture of its performance security, penalty for late delivery, or termination for default if and to the extent that its delay in performance or other failure to perform its obligations under the Contact is the result of an event of Force Majeure.

64.2  	For purposes of this clause, "Force Majeure" means an event beyond the control of the Supplier and not involving the Supplier's fault or negligence and not foreseeable.  Such events may include, but are not restricted to, wars or revolutions fires, floods, epidemics, quarantine restrictions, and freight embargoes.

64.3   	If a Force Majeure situation arises, the supplier will promptly notify the Purchaser in writing of such condition and the cause thereof.  Unless otherwise directed by the Purchaser in writing, the Supplier will continue to perform its obligations under the Contract as far as is reasonably practice, and will seek all reasonable alternative means for performance not prevented by the Force Majeure event.

No price variance will be allowed during the period of force measure.

65.	Settlement of Disputes

65.1	If any dispute or difference of any kind whatsoever will arise between the Purchaser and the Supplier in connection with or arising out of the Contract, the parties will make every effort to resolve amicably such dispute or difference by mutual consultation.

65.2	If, after thirty (30) days the parties have failed to resolve their dispute or difference by such mutual consultation, then either the Purchaser or the Supplier may give notice to the other party of its intention to commence arbitration, as hereinafter provided, as to the matter in dispute, and no arbitration in respect of this matter may be commenced unless such notice is given.

65.3	Any dispute of difference in respect of which a notice of intention to commence arbitration has been given in accordance with this Clause will be finally settled by arbitration.  Arbitration may be commenced prior to or after delivery of the Materials / equipment under the Contract.

65.4	Arbitration proceedings will be conducted in accordance with the following rules of procedure. The dispute resolution mechanism will be as follows:

(a) 	In the case of a dispute or difference arising between the Purchaser and a Supplier relating to any matter arising out of or connected with this agreement, such dispute or difference will be settled in accordance with the Arbitration and Conciliation Act. 1996.  The Arbitral Tribunal will consist of three Arbitrators one each to be appointed by the Purchaser and the supplier the Third Arbitrator will be chosen by the two Arbitrators so appointed by the parties and will acts as Presiding Arbitrator. In case of failure of the two Arbitrators appointed by the parties to reach upon a consensus within period of 30 days from the appointment of the Arbitrator appointed subsequently, the Presiding Arbitrator will be appointed by The Institution of Engineers (India).

- If one of the Parties fails to appoint its Arbitrator in pursuance of Sub-Clause (a) within 30 days after receipt of the notice of the appointment of its Arbitrator by The Institution of Engineers (India), will appoint the Arbitrator.  A certified copy of the order of the Institution of Engineers (India), making such an appointment will be furnished to each to the parties.

- Arbitration Proceedings will be held at Purchaser’s Headquarters, and the language of the Arbitration Proceedings and that of all documents and communication between the parties will be English.

- The decision of the majority of Arbitrators will be final and binding upon both parties.  The cost and expenses of Arbitration Proceedings will be paid as determined by the Arbitral Tribunal.  However, the expenses incurred by each party in connection with the preparation, presentation etc., of its proceedings as also the fees and expenses paid to the Arbitrator appointed by such party or on its behalf will be borne by each party itself.

- Where the value of the Contract is Rs. One Crore and below, the disputes or differences arising will be referred to the Sole Arbitrator.  The Sole Arbitrator should be appointed by agreement between the parties; failing such agreement, by the appointing authority namely The Institution of Engineers (India).

65.5	Notwithstanding any reference to arbitration herein,

- The parties will continue to perform their respective obligations under the Contract unless they otherwise agree; and

- The Purchaser will pay the Supplier any monies due the Supplier.

66.	Jurisdiction

All and any disputes or differences arising out of or touching this contract will be decided by the Courts or Tribunals situated in Purchaser’s Headquarters only. No suit or other legal proceedings will be instituted elsewhere.

67.    	Notices

67.1	Any notice given by one party to the other pursuant to this Contract will be sent to the other party in writing or by cable, telex, or facsimile and confirmed in writing to the other party’s address.

67.2  	A notice will be effective when delivered or on the notice's effective date, whichever is later.

68.	Foreign Exchange

No Foreign Exchange is available or expected for this purchase. Offers which do not require release of F.E. or procurement of import license by TSSPDCL only will be considered. Where some of the components are to be imported the manufacturer will have to make their own arrangements for import license etc., and should not look for any assistance from TSSPDCL.

SECTION-IV

SCHEDULE OF REQUIREMENT

STN-943/2022

| Sl. No. | Description | Qty. (Nos.) | Free at Destination Stores |
| --- | --- | --- | --- |
| 1. | Three phase LTCT meters with 100/5A CTR with 4 CTs in PP Box with Net-metering features DLMS (CAT-C). The following cables shall be supplied One in every 20 Nos. Three Phase Net Meters. - Optical Port to USB - Optical port to CMRI - RS 232 (terminated with RJ11) to USB - RS 232 (terminated with RJ11) to CMRI | 600 | Any district stores In TSSPDCL jurisdiction. |

Note: -

- In e-procurement commercial stage, if F&I charges are applicable then mention whether F&I  charges entered are exclusive/inclusive of GST in the remarks section. If not mentioned in remarks, F&I charges will be considered as inclusive of GST.

- The tenderer should quote the rates for free at destination stores and shall fill the price schedule in e-procurement platform.

3.	2 Nos. (two) samples of  quoted item shall be submitted at the time of submission of bid. Bids received without samples will be rejected.

The purchaser will not be responsible for any damage that may be caused to the samples at                      	any time

4.	Delivery: To commence in 45 days and complete within 3 (THREE) months from the date of receipt of purchase order.

TSSPDCL Stores:

| District | Store Name |
| --- | --- |
| Mahaboobnagar | Mahaboobnagar |
| Nalgonda | Nalgonda |
| Medak | SangaReddy |
| Siddipet | Siddipet |
| RangaReddy | RangaReddy |
| Hyderabad | City-Hyd Stores |
| Wanaparthy | Wanaparthy |
| Suryapet | Suryapet |

SECTION-V

QUALIFICATION REQUIREMENTS

SPECIFICATION No. STN-943/2022

1.	The bidder must possess BIS and ISO certifications The bidder should be a manufacturer who must have designed, manufactured, tested and supplied to power utilities at least 40% of the quoted quantity of the goods / equipment of same or higher class indicated in the “Schedule of material” in one continuous period of 12 months during the last 5 years and its financial turnover during any one year of the last five years should have been equal or more than 100% value of the material now quoted.

At least 20% of similar material offered against this Specification should be in successful operation since 2 years as on the date of opening of the Bid with documentary evidence.

( Performance Certificates issued by head of purchase wing will only be considered)

Fresh bidders can be given order upto 15% of total quantity as a trial order if equipment is justified.

Any company/vendor/supplier/contractor that is blacklisted/debarred by any other power utility is not eligible to participate in the tenders.

The bidders shall have to furnish an undertaking in the prescribed format (at page               no.68) regarding any relation to the promoters of blacklisted / debarred companies by any utility. Any false information furnished in the declaration while rendering bid, such contract is liable for termination as well as recovery of damages.

2.	The bidder should furnish the information on all past supplies and satisfactory performance in proforma under Form 6 attested by a CA.

3.	All bids submitted will also include the following information:

i.	Copies of original documents defining the constitution or legal status, place of registration and principle place of business of the company or firm or partnership, etc.,

ii.	The bidder should furnish a brief write-up, backed with adequate data, explaining his available capacity and experience (both technical and commercial) for the manufacture and supply of the required equipment within the specified time of completion after meeting all their current commitments.

iii.	The bidder should clearly confirm that all the facilities exist in his factory for inspection and testing and these will be made available to the purchaser or his representative for inspection.

iv.	Reports on financial standing of the Bidder such as profit and loss statement, balance sheets and auditor’s report for the past five years, bankers certificates etc.

4.	The bidder shall furnish Type Test Reports. The type tests must have been conducted on the material offered as per the relevant IS/CBIP in recognized NABL laboratory as per the latest revision of the Technical Specification and the date of Type tests will not be later than                     3 years.  In addition to this DLMS CAT-C certification is to be enclosed. The Bids received without type test reports will be treated as Non-Responsive.

5.	Even though the bidder meets the above qualifying criteria, they are subject to be disqualified if they have…

a.	made misleading or false representations in the forms statements and attachments submitted in proof of qualification requirements and / or

b.	record of poor performance such as not properly completing the contract, inordinate delays in supply completion, litigation history or financial failure etc.

### 6.	Not withstanding anything stated above the purchaser reserves the right to assess bidder’s 	capability and capacity to perform the contract should circumstances warrant such an 	assessment in the overall interest of the purchaser.

### 7.	Two (2) Nos. samples of Three phase LTCT meters with 100/5A CTR with 4 CTs in PP  Box with Net-metering features DLMS (CAT-C) programmed as under shall accompany the tender.  Tenders received without samples are liable for rejection.

SECTION-V

TECHNICAL SPECIFICATION STN-943/2022

Three phase LTCT meters with 100/5A CTR with 4 CTs in PP  Box with Net-metering features

1.0 SCOPE :

This specification covers design, engineering, manufacture, assemble, stage testing, inspection and testing before supply and delivery at destination stores of 3 element 4wire C.T Operated L.T Electronic Trivector (DLMS ) Meters of accuracy class 0.5S with PP box with DLMS ICS CAT (C1) Consumer meters ( bi-directional solar net meters) for the purpose of Tariff Metering.

1.1		It is not the intent to specify completely herein all the details of the design and construction of material. However the material shall conform in all respects to high standards of engineering, design and workmanship and shall be capable of performing in continuous commercial operation in a manner acceptable to the purchaser, who will interpret the meanings of drawings and specification and shall have the power to reject any work or material which, in his judgment is not in accordance therewith. The offered material shall be complete with all components necessary for their effective and trouble free operation. Such, components shall be deemed to be within the scope of Bidder’s supply irrespective of whether those are specifically brought out in this specification and/or the commercial order or not.

1.2		It is mandatory that in case of all manufacturers, the offered meter shall be ISI marked and bidder shall have to furnish valid BIS certificate along with the offer.

  - APPLICATION

Consumer meter – DLMS ICS Category “C1”.

- STANDARDS:

- IS-14697:1999(2004) Specification for AC Static Transformer operated Watt Hour & VAR-Hour meters (class 0.5S);

IS-15959:2011 Data Exchange for Electricity Meter Reading Tariff & Load Control – Companion Specification

CBIP - 325 Manual on Standardization of AC Static Electrical Energy Meter

IEC 62052-11 Electricity metering equipment (AC) –General requirements, tests and test conditions -Part 11: Metering equipment; IEC 62053-22 Electricity metering equipment (AC) –Particular requirements - Part-22: Static Meters for Active Energy (Class 0.5S);

IEC 62053-23 Electricity metering equipment (AC) –Particular requirements - Part-23: Static Meters for Reactive Energy;

IS 15707 Specification for Testing, evaluation, installation & maintenance of AC Electricity Meters-Code of Practice.

Guidelines on “Data Exchange for Electricity Meter Reading, Tariff and Load Control – Companion Specification”

IEC 62056-21 Electricity metering: Data exchange for meter reading, tariff and load control- Part 21: Direct local data exchange

| IEC | 62056-31 |  | Electricity metering: Data | exchange for | meter |
| --- | --- | --- | --- | --- | --- |
| reading, | tariff | and | load control -Part 31: Local | Area Network | data |
| exchange |  |  |  |  |  |
| IEC 62056-61 |  | Electricity metering: Data exchange for meter reading, |  |  |  |
| tariff and load control- Part 61: Object identification system (OBIS) |  |  |  |  |  |

IS: 2705/Part I, II & III: Specification for Current Transformers IS:5133 : Specification for boxes for enclosures to electrical accessories

CEA installation and operation of meters regulations with all amendments.

Equipment conforming to other internationally accepted standards which ensure equal or higher quality than the standards mentioned above would also be acceptable. in case of conflict the Guidelines on “Data Exchange for Electricity Meter Reading, Tariff and Load Control – Companion Specification” enclosed with this document as annexure shall prevail upon.

- SERVICE CONDITIONS:

The equipment to be supplied against this Specification shall be suitable for satisfactory continuous operation under the following tropical conditions.

| Sl.No. | Location | At various Sub-stations in the state of Telangana |  |
| --- | --- | --- | --- |
| i) | Max. ambient air temperature (deg.C) | 50 |  |
| ii) | Max. ambient air temperature in a closed (deg.C) | 60 |  |
| iii) | Min. Ambient air temperature (deg.C) | 7.5 |  |
| iv) | Average daily ambient air temperature (deg.C) | 3.5 |  |
| v) | Max. Relative Humidity (%) | 100 |  |
| vi) | Max. altitude above mean sea level (m) | 1000 |  |
| vii) | Average Annual rainfall (mm) | 925 |  |
| viii) | Max. wind pressure (kg/sq.m) | 200 |  |
| ix) | Isoceraunic level (days per year) | 50 |  |
| x) | Seismic level (Horizontal accn.) | 0.10g |  |
| xi) | Noise Level | 45 Db |  |

Moderately hot and humid tropical climate, conducive to rust and fungus growth. The climatic conditions are prone to wide variations in the ambient conditions. Smoke is also present in the atmosphere. Heavy lightning also occurs during June to October

- GENERAL TECHNICAL REQUIREMENTS

- The CT operated meter shall conform to the following specific parameters:

| 1 | Type | AMR Compatible Static, |  |
| --- | --- | --- | --- |
|  |  | 3Ph,4Wire 3X 240V (LTCT) |  |
| 2 | frequency | 50 Hz ± 5% |  |
| 3 | accuracy class | 0.5S for both active &Reactive powers |  |
| 4 | voltage rating | Suitable for operation from 240 V |  |
|  |  | Ph-N, 240 V LT CT (3P, 4W) |  |
| 5 | voltage variation | (-) 40% to (+) 20% |  |
| 6 | basic current (Ib) & current rating | Ib- 5A, Ratio : 100/5 A for LT |  |
|  |  | CT(3P, 4W) |  |
| 7 | maximum continuous current | As per IS 14697:1999(2004) |  |
| 8 | starting current | 0.1% of Ib |  |
|  |  | The active and apparent power |  |
|  |  | consumption, in each voltage |  |
|  |  | circuit, at reference voltage, |  |
|  |  | reference temperature and |  |
|  |  | reference frequency shall not |  |
| 9 | power consumption | exceed 1. 0 W and 4 VA. The |  |
|  |  | apparent power taken by each |  |
|  |  | current circuit, at basic current, |  |
|  |  | reference frequency and |  |
|  |  | reference temperature shall not |  |
|  |  | exceed 1.0 VA. |  |
| 10 | power factor | 0 Lag – Unity – 0 Lead |  |
|  |  | Meter shall be designed with |  |
|  |  | application specific integrated |  |
|  |  | circuit (ASIC) or micro controller; |  |
|  |  | shall have no moving part; |  |
|  |  | electronic components shall be |  |
| 11 | Design | assembled on printed circuit |  |
|  |  | board using surface mounting |  |
|  |  | technology; factory calibration |  |
|  |  | using high accuracy (0.05 class) |  |
|  |  | software based test bench. |  |
|  |  | Assembly of electronic |  |
|  |  | components shall be as per ANSI |  |
|  |  | /IPC-A-610 standard. |  |
|  |  | Manufacturer must have test |  |
| 12 | DLMS test certificate | certificate for conformance to |  |
|  |  | DLMS from CPRI of Category – C1. |  |

However manufacturer can offer meters which can withstand higher variations.

- ACCURACY:

Class of accuracy of meters shall be 0.5S for both active & reactive energies. The accuracy should not drift with time

.

- STARTING CURRENT:

The meter should start registering the energy at 0.1% Ib and unity power factor.

- MAXIMUM CURRENT:

The rated maximum current of the meter shall be 120% Ib at which the meter purports to meet the accuracy requirements.

- MEASUREMENT OF ENERGY:

The meter should be capable of measuring Fundamental Energy as well Total Energy i.e. Fundamental plus Harmonics energy. Total Energy shall be made available on meter-display and the same only shall be used for billing purpose.

- The meter shall be suitable for lag only tariff. In case of lagging loads, KVAH2 = KWH2 + RKVAH2 and with leading load, KVAH2 = KWH2.Thus RKVAH lead contribution shall be blocked.

- CONSTRUCTIONAL REQUIREMENT/ METER COVER & SEALING ARRANGEMENT

- Wherever poly carbonate cover is specified, it shall conform to IS 11731 (FH-1category) besides meeting the test requirement of heat deflection test as per ISO 75, glow wire test as per the IS:11000 (part 2/SEC-1) 1984 OR IEC PUB,60695-2-12, Ball pressure test as per IEC--60695-10-2 and Flammability Test As per UL 94 or As per IS 11731(Part-2) 1986.

- CONSTRUCTION

The case, winding, voltage circuit, sealing arrangements, registers, terminal block, terminal cover & name plate etc. shall be in accordance with the relevant standards. The meter should be compact & reliable in design, easy to transport & immune to vibration & shock involved in the transportation & handling. The construction of the meter should ensure consistence performance under all conditions especially during heavy rains / very hot weathers. The insulating materials used in the meter should be non-hygroscopic, non-ageing & have tested quality. The meter should comply latest technology such as Microcontroller or Application Specific Integrated Circuit (ASIC) to ensure reliable performance. The mounting of the components on the PCB should compulsorily be Surface Mounted Technology (SMT) type. Power supply component may be of PTH type. The electronic components used in the meter should be of high quality and there should be no drift in the accuracy of the meter for at least ten years. The circuitry of the meter should be compatible with 16 Bit (or better) ASIC with compatible processor and meter should be based on Digital measuring and sampling technique.

The meter should be housed in a safe, high grade, unbreakable, fire resistant, UV stabilized virgin Polycarbonate/ High Grade Engineering Plastic/Thermosetting Plastic casing of projection mounting type. The meter cover should be transparent, for easy reading of displayed parameters, and observation of operation indicators. The meter base may or may not be transparent, but it should not be black in colour. The meter casing should not change shape, size, and dimensions when subjected to 200 hrs on UV test as per ASTMD 53. It should withstand 650 deg. C. glow wire test and heat deflection test as per ISO 75.

- METER CASE AND COVER

The meter should be sealed in such a way that the internal parts of the meter becomes inaccessible and attempts to open the meter shall result in viable damage to the meter cover. This is to be achieved by using continuous Ultrasonic welding on the Meter body, fully flushed between case and cover. In case, ultrasonic welding using plate/strip is used the material of plate/strip should be same as that of cover and base and the strip should flush with meter body. The manufacturers logo should be embossed on the strip / plate. The meter cover should be fixed to the meter base (case) with Unidirectional Screws, so that the same cannot be opened by use of screwdrivers. The meter shall withstand external magnetic influence as per latest amendments of CBIP 325.

- GENERAL :

    - Meters shall be designed and constructed providing reinforced insulation in such a way so as to avoid causing any danger during use and under normal conditions. However, the following should be ensured :

      - Personnel safety against electric shock.

      - Personnel safety against effects of excessive temperature.

      - Protection against spread of fire.

      - Protection against penetration of solid objects, dust and water.

    - All insulating materials used in the construction of meters shall be non-hygroscopic, non-ageing and of tested quality. All parts that are likely to develop corrosion shall be effectively protected against corrosion by providing suitable protective coating.

  - The meter shall have an operation indication device such as a blinking LED/LCD. The operation indicator shall be visible from the front window.

  - The meter shall conform to the degree of protection IP 51 of IS 12063/ IEC:529 and IEC:60529 for protection against ingress of dust, moisture and vermins.

  - The meter shall be supplied with a transparent extended terminal-block cover (ETBC).

  - The meter terminal block, the ETBC and the meter case shall ensure reasonable safety against the spread of fire and should not be ignited by thermic overload of live parts in contact with them.

  - The terminal block shall be of high grade non-hygroscopic, fire-retardant, low-tracking, fire-resistant, high grade engineering plastic (not Bakelite) which should form an extension of the meter case, meeting the requirement of clause No.6.4 of IS:14697 / Clause No.

    - of IEC 1036-1996.

  - A separate test terminal block is required.

- TERMINAL ARRANGEMENTS:

The terminals in the terminal block shall be of adequate length in order to have proper grip of conductor with the help of screw adjustable metal plates to increase the surface of contact and reduce the contact resistance. The screws shall have thread size not less than M 4 and head having 4-6mm. diameters. The screws shall not have pointed ends at the end of threads. All terminals and connecting screws should be of tinned/nickel plated brass material. The terminals shall be marked properly on terminal block for giving external connections. The internal diameter of terminal hole should be minimum 5.5 mm. The holes in the insulating material shall be of sufficient size to accommodate the insulation of conductor also. The terminal cover shall be transparent High grade Engineering Plastic/Polycarbonate/ Thermosetting Plastic with minimum thickness 2.0 mm and the terminal cover shall be of extended type completely covering the terminal block and fixing holes. The space inside the terminal cover should be sufficient to accommodate adequate length of external cables. A diagram of connections should be provided inside the cover of terminal block. The terminal cover shall be extended such that when it is placed in position it is not possible to approach the connections or connecting wires. The terminals and the screws shall be suitable to carry up to 150% of Imax safely. The terminals shall have suitable construction with barriers and covers to provide secure and safe connections of Current Transformers and Voltage Transformers leads of stranded copper conductors.

- SEALING OF METER:

Proper sealing arrangement should be provided on meter to make it tamper proof and avoid mishandling by unauthorized persons. Meters must be supplied with 2 (two) nos. manufacturer seals between meter base and meter cover at both the sides. The meter terminal block with minimum 1 number sealing screw and one number separate sealing arrangement to the MD reset push button. The RS232 port & optical port should have proper sealing arrangement. The meter should be designed and constructed in such manner to make it pilfer proof once it is sealed. Bidder shall provide patented seals as per CEA Regulation (2006).

5.7	MANUFACTURING PROCESS, ASSEMBLY AND TESTING:

Meters shall be manufactured using latest and „state of the art technology and methods prevalent in electronics industry. The meter shall be made from high accuracy and reliable surface mount technology (SMT) components. All inward flow of major components and sub assembly parts (CT, PT, RTCs / Crystal, LCDs, LEDs, power circuit electronic components etc.) shall have batch and source identification. Multilayer PCB assembly with PTH using surface mounted component shall have adequate track clearance for power circuits. SMT component shall be assembled using automatic „pick-and-place‟ machines, Reflow Soldering oven, for stabilized setting of the components on PCB. For soldered PCBs, cleaning and washing of cards, after wave soldering process is to be carried out as a standard practice. Assembly line of the manufacturing system shall have provision for testing of sub-assembled cards. Manual placing of components and soldering, to be minimized to items, which cannot be handled by automatic machine. Handling of PCB with ICs / C-MOS components, to be restricted to bare minimum and precautions to prevent ESD failure. Complete assembled and soldered PCB should undergo functional testing using Computerized Automatic Test Equipment. Fully assembled and finished meter shall undergo “burn-in” test process for 24 Hours at 55 degree Celsius (Max. temperature to not exceed 60 degree Celsius) under base current (Ib) load condition. Test points should be provided to check the performance of each block/stage of the meter circuitry.

RTC shall be synchronized with NPL time at the time of manufacture. Meters testing at intermediate and final stage shall be carried out with testing instruments, duly calibrated with reference standard, with traceability of source and date.

- ENVIRONMENTAL ASPECTS:

Meter shall be designed and constructed to be capable of withstanding all severe stresses and vibration and dust environments likely to be encountered in actual practice as the meter will be installed outdoor in boxes.

If any special precautions etc. are required as the meters are supposed to be installed in outdoor you may please specify them.

- IMMUNITY TO ELECTRO MAGNETIC DISTURBANCE:

The meter shall be designed in such a way that conducted or radiated electromagnetic disturbance as well as electrostatic discharge do not damage or substantially influence the meter. The test report from any standard lab conducting the test as prescribed in the CBIP -325 with latest ammendments and IS 14697 and test result to be submitted.

- MEASURING PARAMETERS:

The meter should be capable of measuring the following electric parameters of poly phase supplies in all power factors lagging or leading. The meter should measure 'kWh' and ‘kVArh’ continuously. It should compute kVAh in such a fashion that the leading power factor should be ignored i.e. kVAh calculation is based on Lag only.

  - The parameters kWH, kVARH, kVAH and max. demand in Import and Export ,Net energyshall be displayed continuously in cyclic order on the meter to enable the Board/consumer to know the above parameters at any instant.

  - At the start of each sequence of display LED/LCD healthiness anomaly shall be displayed.

- Display Parameter

AUTO MODE:

LCD Segment Check

Battery Status

Meter Sl.No

Date

Time

Self Diagnostic Flags

Connection Check

Present Voltage and Current Status AND Phase Sequence (Voltage) AND Current Sequence

R-Ph. Voltage

Y-Ph. Voltage

B-Ph. Voltage

R-Ph. Current

Y-Ph. Current

B-Ph. Current

Supply Frequency

Signed Inst. PF

Inst. Signed Active Power

Inst. Signed Reactive Power

Inst. Signed Apparent Power

Cumulative Active Energy Import

Cumulative Active Energy export

Cumulative Net Active Energy (Import-Export)

Cumulative Apparent Energy import

Cumulative Apparent Energy export

Cumulative Reactive Import lag

Cumulative Reactive Import lead

Cumulative Reactive export lag

Cumulative Reactive export lead

Raising Demand in KVA Import with elapsed time

Raising Demand in KVA export with elapsed time

TOD 0-24 Hrs KVA Import

TOD 0-24 Hrs KVA Import Date and Time

TOD 0-24 Hrs KVA Export

TOD 0-24 Hrs KVA Export Date and Time

TOD 0-24 Hrs KW Import

TOD 0-24 Hrs KW Import Date and Time

TOD 0-24 Hrs KW Export

TOD 0-24 Hrs KW Export Date and Time

Cumulative MD in KVA Import

Cumulative MD in KVA Export

Cumulative MD in KW Import

Cumulative MD in KW Export

MD Reset Count

Total Tamper Count

CT Ratio

Present CT Status

Present PT Status

Present Others Status

Version

R-Ph. Voltage THD

Y-Ph. Voltage THD

B-Ph. Voltage THD

R-Ph. Current THD

Y-Ph. Current THD

B-Ph. Current THD

TOD Zone wise energies(import, export)

TOD Zone wise MD’s(import, export)

PUSH BUTTON MODE:

LCD Segment Check

Battery Status

Meter Sl.No

Date

Time

Self Diagnostic Flags

Connection Check

Present Voltage and Current Status AND Phase Sequence (Voltage) AND Current Sequence

R-Ph. Voltage

Y-Ph. Voltage

B-Ph. Voltage

R-Ph. Current

Y-Ph. Current

B-Ph. Current

Supply Frequency

Signed Inst. PF

Inst. Signed Active Power

Inst. Signed Reactive Power

Inst. Signed Apparent Power

Cumulative Active Energy Import

Cumulative Active Energy export

Cumulative Net Active Energy (Import-Export)

Cumulative Apparent Energy import

Cumulative Apparent Energy export

Cumulative Reactive Import lag

Cumulative Reactive Import lead

Cumulative Reactive export lag

Cumulative Reactive export lead

Raising Demand in KVA Import with elapsed time

Raising Demand in KVA export with elapsed time

TOD 0-24 Hrs KVA Import

TOD 0-24 Hrs KVA Import Date and Time

TOD 0-24 Hrs KVA Export

TOD 0-24 Hrs KVA Export Date and Time

TOD 0-24 Hrs KW Import

TOD 0-24 Hrs KW Import Date and Time

TOD 0-24 Hrs KW Export

TOD 0-24 Hrs KW Export Date and Time

Cumulative MD in KVA Import

Cumulative MD in KVA Export

Cumulative MD in KW Import

Cumulative MD in KW Export

MD Reset Count

Total Tamper Count

CT Ratio

Present CT Status

Present PT Status

Present Others Status

Version

R-Ph. Voltage THD

Y-Ph. Voltage THD

B-Ph. Voltage THD

R-Ph. Current THD

Y-Ph. Current THD

B-Ph. Current THD

Average PF

H1 Average PF

R-Ph PT Miss Count

Y-Ph PT Miss Count

B-Ph PT Miss Count

R-Ph CT Open Count

Y-Ph CT Open Count

B-Ph CT Open Count

Voltage Unbalance Count

Current Unbalance Count

R-Ph CT Reversal Count

Y-Ph CT Reversal Count

B-Ph CT Reversal Count

Programming Count

Cumulative Present CT Status

Cumulative Present PT Status

Cumulative Present Others Status

First Occurrence Tamper ID

Time of 1st Tamper Occurrence

Date of 1st Tamper Occurrence

Last Occurrence Tamper ID

Time of Last Tamper Occurrence

Date of Last Tamper Occurrence

Last Restoration Tamper ID

Time of Last Tamper Restoration

Date of Last Tamper Restoration

Cumulative Fund. KWH Import

Cumulative Fund. KWH Export

H1 Active Import Energy

H2 Active Import Energy

H3 Active Import Energy

H4 Active Import Energy

H5 Active Import Energy

H6 Active Import Energy

H1 Active Export Energy

H2 Active Export Energy

H3 Active Export Energy

H4 Active Export Energy

H5 Active Export Energy

H6 Active Export Energy

H1 Apparant Import Energy

H2 Apparant Import Energy

H3 Apparant Import Energy

H4 Apparant Import Energy

H5 Apparant Import Energy

H6 Apparant Import Energy

H1 Apparant Export Energy

H2 Apparant Export Energy

H3 Apparant Export Energy

H4 Apparant Export Energy

H5 Apparant Export Energy

H6 Apparant Export Energy

H1 MD in KW Import

H2 MD in KW Import

H3 MD in KW Import

H4 MD in KW Import

H5 MD in KW Import

H6 MD in KW Import

H1 MD in KW Export

H2 MD in KW Export

H3 MD in KW Export

H4 MD in KW Export

H5 MD in KW Export

H6 MD in KW Export

H1 MD in KVA Import

H2 MD in KVA Import

H3 MD in KVA Import

H4 MD in KVA Import

H5 MD in KVA Import

H6 MD in KVA Import

H1 MD in KVA Export

H2 MD in KVA Export

H3 MD in KVA Export

H4 MD in KVA Export

H5 MD in KVA Export

H6 MD in KVA Export

TOD Zone wise energies(import, export)

TOD Zone wise MD’s(import, export)

HR MODE:

HR Cumulative Active Energy Import

HR Cumulative Reactive Import lag

HR Cumulative Reactive Import lead

HR Cumulative Apparent Energy import

HR Cumulative Active Energy export

HR Cumulative Reactive export lag

HR Cumulative Reactive export lead

HR Cumulative Apparent Energy export

HR Raising Demand in KVA Import with elapsed time

HR Raising Demand in KVA export with elapsed time

BATTERY MODE: - Total Active Import Energy Register - Total Active Export Energy Register - Apparent While Active Import Energy Register - Apparent While Active Export Energy Register - MD in KVA import - MD in KVA export - Cumulative MD in KVA Import - Cumulative MD in KVA export - MD Reset or Bill count - TOD Apparent While Active Import Energy Register (Reg 1 ) - TOD Apparent While Active Import Energy Register (Reg 2 ) - TOD Apparent While Active Import Energy Register (Reg 3 ) - TOD Apparent While Active Import Energy Register (Reg 4 ) - TOD Apparent While Active Import Energy Register (Reg 5 ) - TOD Apparent While Active Import Energy Register (Reg 6 ) - TOD Apparent While Active Import MD Register (Reg 1 ) - TOD Apparent While Active Import MD Register (Reg 2 ) - TOD Apparent While Active Import MD Register (Reg 3 ) - TOD Apparent While Active Import MD Register (Reg 4 ) - TOD Apparent While Active Import MD Register (Reg 5 ) - TOD Apparent While Active Import MD Register (Reg 6 ) - Net energy Note:Total data download shall be made possible even in battery mode also using a CMRI/Laptop

5.11	Read out Parameters with CMRI/ RMR :

The Read out parameters with CMRI/ RMR should be present in the meter as per ICS 15959 Cat C1 and all the above mentioned parameters.

- MAXIMUM CURRENT:

The maximum current of the meter is 120% Ib at which the meter purports to meet the accuracy requirements.

- DIPLAY:

The meter display shall have 7 digits(complete) for energy counter with alphanumeric digits for parameter identifier and tamper indication with backlit Liquid Crystal Display (LCD) of minimum 10 mm height, wide viewing angle suitable for temperature withstand of 70° C. LCD to be of STN (super twisted numetic) type construction. No decimal is required for main KWh, KVAh, KVarh (lag & lead) display. The data stored in the meters shall not be lost in the event of power failure. The meter shall have Non Volatile Memory (NVM), which does not need any battery backup. The NVM shall have a minimum retention period of 10 years. Meter shall have Scroll Lock facility to display any one desired parameter continuously from display parameters. Auto display cycling of each parameter should be minimum 10-12 Seconds. The auto display cycles shall be continuous. OBIS code in display is optional. It should be possible to easily identify the single or multiple displayed parameters through symbols/legend on the meter display itself or through display annunciation.

Push button mechanism should be of high quality and should provide trouble free service for a long span of time. Up and Down scrolling facility should be there for Push Button Mode.

- DISPLAY RESOLUTION :

| 1. | Voltage | = | 0.1V |
| --- | --- | --- | --- |
| 2. | Current | = | 0.01A |
| 3. | P.F. | = | 0.001 |
| 4. | Energy | = | 0.001 KWH/KVARH/KVAH |
| 5. | Demand | = | 0.1 KVA / KW |

  - MAXIMUM DEMAND REGISTRATION:

The maximum demand is to be monitored during each demand interval set (30 minutes) and the maximum of these in a month shall be stored. Whenever MD is reset the maximum MD value so registered shall be stored along with date and time. Under the current integration period, the rising demand should be displayed continuously along with the elapsed time. The registered demand and the number of times the MD is reset shall also be displayed and the information stored.

- MD RESET:

The meter should have provision of auto / manual maximum demand resetting.

    - Manually by operation of a button which is to be covered and sealing provision available for such cover.

    - Provision for automatic resetting at the end of the month at 24.00 hrs may be made available.

    - Manual MD reset facility shall be allowed only once in a day.

- OUTPUT DEVICE:

Energy Meter shall have test output, accessible from the front, and be capable of being monitored with suitable testing equipment while in operation at site. The operation indicator must be visible from the front and test output device shall be provided in the form of LED. Resolution of the test output device shall be sufficient to enable the starting current test in less than 10 minutes. Minimum gap should be maintained between Active & Reactive Test LED.

Note: In the absence of power supply, facility for display of meter reading should be available.

6.5	REAL TIME INTERNAL CLOCK (RTC)

RTC shall be pre-programmed for 15 Years Day/date without any necessity for correction. The maximum drift shall not exceed ± 300 Seconds per year. The clock day/date setting and synchronization shall only be possible through password/Key code command from one of the following:

  - Hand Held Unit (HHU) or directly through BCS and this shall authentication from BCS for individual meter.

  - From remote server through suitable communication network with authentication from BCS.

- SELF DIAGNOSTIC FEATURES:

The meter shall be capable of performing complete self-diagnostic check to monitor the circuits for any malfunctioning to ensure integrity of data memory location all the time. If possible, the details of malfunctioning should be recorded in the meter memory. The bidder should furnish the details of self-diagnostic capability feature, viz (i) Memory status, (ii)Battery status (iii) NVM & (iv) and it should be in display.

- LOAD SURVEY CAPABILITY:

The meter should be capable of recording load survey data of Phase wise Voltage, Phase wise current, Active Energy and Apparent Energy ,Power Factor(phase wise and total), kVArh Lag, kVArh Lead, Max. demand KW& kVA.for a period of minimum 60 days for 30-minute integration period. Real time & date should be shown in all the load survey graphs and table. It should be possible to transfer this data on to a base Computer station (to be provided by the Purchaser) through CMRI.  The base computer shall give complete details of load survey particulars both in numeric data form and in graphic form.  Necessary software for invoking the base computer station shall be provided by the bidder and demonstrated along with communication cables.  The solar hours (6AM to 6PM) and non solar hours (6PM to 6AM) energies (kwh, KVah) in import and export shall also be given in midnight snapshots.

- TIME OF DAY TARIFF / DEMAND:

The meter offered shall contain provisions for multiple tariff metering ( time of day metering / demand ) . The meter offered should have a real time clock based on a quartz crystal with a battery totally independent of power supply. The meter shall be capable of being set in to minimum of 8 time zones ( optionally more time zones can be offered) in 24 hours cycle to cover morning and evening on and off peak periods separately bb register shall be provided for active energy and demand data.

Initially TOD registers for 6 time zones by default shall be programmed as detailed below to capture KWh, KVAh & KVA.

T1: 00.00 hrs. to 06.00 hrs.

T2: 06.00 hrs. to 10.00 hrs.

T3: 10.00 hrs. to 14.00 hrs.

T4: 14.00 hrs. to 18.00 hrs.

T5: 18.00 hrs. to 22.00 hrs.

T6: 22.00 hrs. to 24.00 hrs.

and it should be possible for TSSPDCL to invoke / change them through the use of CMRI with 2 level password protection and necessary software should be loaded by the meter supplier into the base computer station. The above time zones should be non-operative and make them operative with CMRI by the meter manufacturer at free of cost as and when required by TSSPDCL.

- COMMUNICATION CAPABILITY:

The meter shall be provided with two ports for communication of the measured/collected data. The hardware port (with sealing facility) compatible with RS 232 with RJ11 specifications which shall be used for remote access through suitable Modem and Optical port. RS232 with RJ11 shall be used for local data downloading through a DLMS protocol with HHU or direct through BCS. Both ports shall support the default and minimum baud rate of 9600 bps.

Data downloading time from meter to HHU/PC should be within 2 min for meter data (without load survey) and within 10 min for meter data with load survey.

2 Nos. cables (Flexible shielded universal cable of length 1500 mm ± 10 mm having (i) 9 pin D-type connector with electrical circuit and (ii) RJ11 Cables to facilitate downloading of meter data, either on to CMRI/HHU /Laptop for each 20 Nos. meters is required.

- HAND HELD UNIT (HHU): Not required

- BASE COMPUTER SOFTWARE (BCS):

The BCS should be user friendly. Latest version of Windows based BCS shall be supplied. The data transfer should be reliable and fraud proof. BCS should give all details pertaining to billing and load survey data. The meter condition details should also be transferred into the BCS including abnormalities/anomalies of voltage current conditions or tamper conditions which can occur due to mistake in connections or intentionally done for the purpose of tamper. The software should show electrical conditions existing at the time of reading the meter in tabular forms as well as in graphical format (Phase diagram) i.e. Phase diagram is required for voltage, current & PF only. All the information about energy, maximum demand and their respective TOD register readings, billing register readings and billing history readings should be shown in a manner which user can understand quickly, preferably in tabular format. All the load survey data should be available in numerical as well as graphical format. It should also be possible to view this data in daily, weekly and monthly formats. The load survey graph should show values. All the information about tamper events should be accompanied with date and time stamping along with the SNAPSHOT (details) of the respective electrical conditions. This information should be displayed in the sequence in which it happened, in cumulative format as well as in summary format. The cumulative format should segregate a particular tamper information and summary report should show count of tamper occurrence, restoration and the duration for which meter has remained under tamper condition.  . All tamper snap shots shall consist of phase wise voltages, currents, p.f, KWh (I&E), KVAh (I&E) .  In display, first tamper occurrence & last tamper occurrence & restoration with date & time and total tamper count must be available.

The software should be capable of preparing CMRI/Laptop to read the meter information or to reconfigure the meter for change the setting of the meter as per IS 15959:2011. The BCS should have the facility for ASCII conversion of all recorded meter data. There should be user friendly approach for viewing meter data for the reading collected now or for the reading collected in the past. All information about a particular consumer should be segregated and available at one place so that locating any consumer's past data is easy. It should be possible to locate/retrieve data on the basis of one of the following particulars:

- Consumer ID/Number.

- Meter Sr. No.

- Date of meter reading.

- Location.

The BCS shall have multi level password for data protection and security. The first level should allow the user to enter the system. The different software features shall be protected by different passwords. The configuration of passwords should be user definable. The software installed on one PC should not be copy-able on to another PC.

It is very important that the BCS has the feature to export available data to ASCII format for integrating with the TSSPDCL billing system. Here again a wizard should be available whereby user can select file format (for ASCII), what data to export, the field width selection (whether 8 characters or 10 characters, to include decimal point or not, number of digits after decimal point etc).

Help should be available with the software so that user can use all the features of the software by just reading the Help contents.

- Data Security: The meter manufacturers are responsible for maintaining the security software up to down loading to the base computer station.

- ENVIRONMENTAL ASPECTS:

Meter shall be designed and constructed to be capable of withstanding all severe stresses and vibration and dust environments likely to be encountered in actual practice as the meter will be installed outdoor in boxes.

If any special precautions etc. are required as the meters are supposed to be installed in outdoor you may please specify them.

- NAME PLATE MARKING:

Every meter shall have a nameplate clearly visible and indelible and distinctly marked in accordance with the relevant Standard mentioning “Category – C”. The following information should appear on an external plate attached to the meter cover. i) Manufacturers Name or trademark and place of manufacture. ii) Designation of type. iii) Number of phases and wires. iv) Serial number of meter. v) Month and year of manufacture. Vi) Principal unit of measurement. vii) P.T. Ratio. viii) Basic Current and rated maximum current. ix) C.T. Ratio. x) Reference frequency in Hz. xi) Meter constant (impulse/unit). xii) Class index of meter. xiii) Reference temperature. xiv) “Property of TSSPDCL” xv) Purchaser‟s Order No. & Date. xvi) Guarantee for 5 years from the date of receipt at destination stores xvii) Sign. of insulation. xviii) Bar coding of Serial Number, month & year of manufacture. The name plate shall be provided in such a manner that it is not exposed to the open and is secured against removal.

- IMMUNITY TO ELECTRO MAGNETIC DISTURBANCE:

The meter shall be designed in such a way that conducted or radiated electro- magnetic disturbance as well as electrostatic discharge do not damage or substantially influence the meter. The test report from any standard lab conducting the test as per CBIP325 with latest ammendments and test results submitted.

12.0 PERFORMANCE UNDER INFLUENCE QUANTITIES

The meters performance under influence quantities shall be governed by IS 14697:1999 (2004). The accuracy of meter shall not exceed the permissible limits of accuracy as per standard IS 14697:1999(2004)

- GUARANTEED TECHNICAL PARTICULARS:

The technical particulars as detailed in the specification shall be guaranteed and a statement of guaranteed technical particulars shall be furnished in format along with the tender.

14.0	TAMPER & FRAUD MONITORING FEATURES:

The meter shall work satisfactorily under presence of various influencing conditions like External Magnetic Field, Electromagnetic Field, Radio Frequency Interference, Vibrations, Harmonic Distortion, Voltage/Frequency Fluctuations, and Electromagnetic High Frequency Fields etc. The meter shall be immune to abnormal voltage/frequency generating devices and shall record the occurrence and restoration of all tampers and related snapshots .The tamper logics and thresholds shall be followed as per the logics given by TSSPDCL which is given below.

The accuracy of meter should not be affected with the application of abnormal voltage/ frequency generating device such as spark discharge of approximately 35 kV. The meters should work even in the presence of any two Potential wires. Meter should work correctly irrespective of phase sequence.

Tamper details shall be stored in internal memory for retrieval by authorized personnel through either of the following: a) DLMS compliant HHU. b) Remote access through suitable communication network. c) Direct by PC. Meter should have a continuous and clear indication / annunciation in its display if top cover is removed/open and even refixed (non roll over) and only cover open must be logged in BCS without any restoration. Auto scroll display shall still be there with that COVER OPEN indication at the top of regular display.

The meter should have features to detect the occurrence and restoration of, at least, the following common abnormal events:

- Missing Potential: The meter shall be capable of detecting and recording occurrence and restoration with date and time the cases of Potential failure (one phase or two phases).

- Current imbalance: The meter shall be capable of detecting and recording occurrence and restoration with date and time of Current unbalance (for more than a defined persistence time).

- Current Reversal: The meter shall be capable of detecting and recording occurrence and restoration with date and time if the current is flowing in reverse direction in one or two phases. The meter shall record active energy in forward direction even if one or more CT’s are reversed.  The current vector direction shall always be considered as positive ( import)  for the computation of 3 phase active energy which shall be added in the main active energy ( import) register. The meter shall also record apparent energy in forward direction even if one or more CT’s are reversed.

- Power on/off: The meter shall be capable to record power on /off events in the meter memory. All potential failure should record as power off event. As per DLMS spec, tamper is to be recorded by the meter.

- Magnetic Influence - The meters shall be immune to tampering through application of external magnetic fields as per CBIP-325 with latest amendments.

In the event of logging of presence of abnormal magnetic induction with date & time the positive variation of error may be beyond the limit of 4% but not exceeding a value(e) as given in Note 3.2 under Table 17 (CBIP 325), corresponding to nominal registration of the meter at reference voltage, 150% maximum current and cosØ/sinØ =1, for active/reactive energy meters respectively.

- Voltage unbalance – Meter shall detect voltage unbalance if there is unbalance in voltages.

- Over Current – When load condition at any phase i.e. Line current at any phase goes more than defined limit , this will be detected as Over current condition.

- CT Open – The meter should detect phase wise current circuit open when the circuit is opened from meter side.

- CT Bypass – The condition should be detected whenever the current terminal is bypassed in the meter

- Neutral Disturbance – The meter should detect neutral disturbance if any spurious signal is applied at the meter’s neutral.

- High and Low Voltage: The meter should detect under and over voltage events respectively if voltage falls / rise from defined limits.

- Cover Open: The meter shall be able to detect cover open occurrence event if cover is opened in mains on or off condition. Separate legend for cover open event shall be made available on LCD. This legend shall remain in on state till meter reading so that it will come in to notice of meter reader

- Abnormal Frequency

The above shall be selectable and will be in line with IS 15959 : Data Exchange for Electricity Meter Reading, Tariff and Load Control – Companion Specification

A Minimum 200 numbers of events preferable (compartment wise) i.e. 100 no. events for occurrences & 100 no. events for restoration with date & time and snapshot should be available in the meter memory. Default occurrence and restoration time shall be 5 minutes.75 Events shall be given for current related events and 75 Events shall be given for voltage related events and the balance 50 events shall be for other related events.

All the tamper information logged by the meter should be available in BCS with snapshot, Date & Time as per the tamper logics provided by TSSPDCL with occurrence and restoration.

| LT CT Operated Solar Net Energy Meters |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Sl. No. | Type of tamper | Requirement | Occurrence |  | Restoration |  |  |  |
|  |  |  | Voltage | Current | Voltage | Current |  |  |
| 1 | Missing Potential | Phase Wise | Vx<10% of Vref irrespective other phase Voltage. | lx > 1% Ib Where x is Tampered Phase | Vx>40% vref irrespective to any other phase | - |  |  |
| 2 | High Voltage | - | > 115% of Vref | - | <110% of Vref. | - |  |  |
| 3 | Low Voltage | - | 0 > Vref<75% of Vref. | - | >80% of Vef. | - |  |  |
| 4 | Potential Unbalance | - | (Vmax-Vmin) > Threshold value of Vef. (10%) | No minimum Current Reqd | (Vmax-Vmin) < Thrshold value of Verf. (10%) | No minimum Current Reqd |  |  |
| 5 | Over Current | - | - | >2 times of Ib | - | <2 times of Ib |  |  |
| 6 | Current Unbalance | - | - | (Imax - I min)>20% Ib | - | (Imax - I min)<20% Ib |  |  |
| 7 | Low PF | - | - | lr or ly or lb > 5% Base Current with PF < 0.5 | - | lr or ly or lb > 5% Base Current with PF > 0.5 |  |  |
| 8 | Current Reversal | Phase Wise | - | lx>5% Base Current, direction of current reverse and PF value > 0.2 | - | lx>5% Base Current, direction of current forward and PF value > 0.2 |  |  |
| 9 | CT Missing | Phase Wise | Vref > 10% of Vref. | lx<1% of Base Current & in other 2 phases Ix>10% of Ib. | Vref > 10% of Vref. | lx>10% of Base Current |  |  |
| 10 | CT Open | Phase Wise | - | Ix<2% of base current & in other 2 phases Ix>3% of Ib | - | Avg Current of all 3 phases > 10 % of I basic |  |  |
| 11 | CT By-pass | - | - | Vector sum of (Ir+Iy+Ib-In) > 10% Ib & Iph > 2%Ib in all phases | - | Vector sum of (Ir+Iy+Ib-In) < 10% Ib & Avg Current of all 3 phases > 10 % of I basic |  |  |
| 12 | Magnetic Tamper | - | - | - | - | No minimum Current Reqd |  |  |
| 13 | Power OFF | - | V=0 in all three phases | - | - | - |  |  |
| 14 | Meter Cover Open | - | - | - |  |  |  |  |
|  | Invalid Voltage | - | PT missing event should not persists. Phase angles deviated >±10° from their respective fundamental values. | - | Phase angles deviated <±10° from their respective fundamental values. | - |  |  |
| 16 | Neutral Disturbance | (a) Chopped Signal- if any spurious signal injected to the neutral of meter, either offered meter will be immune or if gets affected it will log the event & register energy on reference voltage, actual current & UPF. |  |  | When normalcy obtained. | - |  |  |
|  |  | (b) If any one of the phases and neutral gets interchanged the accuracy should not be affected and it shall be immune and also it should log the event with snap shot. |  |  |  |  |  |  |
| 17 | Invalid Phase Association | - | When voltage & current sequence is different. | - | When voltage & current sequence is same. | - |  |  |
| 14 | Meter Cover Open | - | - | - |  |  |  |  |
| 15 | Invalid Voltage | - | PT missing event should not persists. Phase angles deviated >±10° from their respective fundamental values. | - | Phase angles deviated <±10° from their respective fundamental values. |  | - |  |

| 14. Meter Cover Open | - | - | - |  |  |
| --- | --- | --- | --- | --- | --- |
| 15. Invalid Voltage | - | PT missing event should not persists. Phase angles deviated >±10° from their respective fundamental values. | - | Phase angles deviated <±10° from their respective fundamental values. | - |
| 16.Neutral Disturbance | (a) Chopped Signal- if any spurious signal injected to the neutral of meter, either offered meter will be immune or if gets affected it will log the event & register energy on reference voltage, actual current & UPF. | When normalcy obtained. | - |  |  |
|  | (b) If any one of the phases and neutral gets interchanged the accuracy should not be affected and it shall be immune and also it should log the event with snap shot. |  |  |  |  |
| 17.Invalid Phase Association | - | When voltage & current sequence is different. | - | When voltage & current sequence is same. | - |

15.0	TESTS:

  - TYPE TESTS FOR METERS:

Meters shall be fully type tested as per relevant Standard (latest version). The type test certificates should be submitted along with the offer. Offer without Type Test Report shall be liable for rejection. The equipment offered (i.e., meters,Box and CTs where applicable) shall be fully type tested at any of the Govt. accredited NABL laboratories by the Bidder as per the relevant standards. The Bidder shall furnish one set of type test reports along with the bid. The date of type tests shall be not older than 3 years as on the date of Bid submission. Bids without type test reports will be treated as non responsive.

The DLMS conformance latest certificate should also be enclosed (Confirms to DLMS-ICS-Cat-C1 specification).

Type tests for trivector meters: As per IS 14697and magnetic tests as per CBIP 325 / IEC-687 and IS:15959:2011 (with latest amendments)

- TESTS FOR CURRENT TRANSFORMERS:

- As per IS-2705/1992(part-I, II & III)

- TESTS FOR BOXES:

As per IS 14722 and in addition the box material will be tested for withstanding temperatures of boiling water for 5 minutes continuously for non distortion or softening of the material. The successful bidder shall submit the test reports for box within two weeks of clear purchase order.

- ACCEPTANCE AND ROUTINE TESTS:

All acceptance tests as stipulated in the relevant standards shall be carried out by the supplier in presence of purchaser’s representative.

All routine tests as in the relevant standards shall be carried out and routine test certificates shall be submitted to each consignee while dispatching the material.

The purchaser reserves the right to insist for witnessing the acceptance/routine testing.

The following shall constitute acceptance test for box:

i).	Physical verification of dimensions of the box.

ii). Compatibility of the box for housing the meter, and CTs where applicable and ensuring ease of connecting and reading the meter.

- Tests during manufacture: The Bidder shall furnish details of tests carried out during the process of manufacture and end inspection by the bidder to ensure the desired quality of the equipment to be supplied.

- ADDITIONAL TESTS:

The purchaser reserves the right of having at his own expenses any other tests(s) of reasonable nature carried out at Bidders premises, at site, or in any other place in addition to the aforesaid type, acceptance and routine tests, to satisfy himself that the material comply with the specifications.

In case of failure in any type test, the supplier is required to modify the design of the material and the material shall be type tested again for the modified design, without any extra cost to the purchaser. No delivery extension shall be given for this additional testing.

The entire cost of testing for the acceptance and routine tests and tests during manufacture shall be treated as included in the quoted unit price.

- TEST REPORTS / TEST CERTIFICATES:

Record of routine test reports shall be maintained by the Bidder at his works for periodic inspection by the purchaser’s representative.

Test certificates of tests conducted during manufacture shall be maintained by the Bidder. These shall be produced for verification as and when desired by the purchaser.

- TEST FACILITIES:

The tests shall be carried out as per relevant Standards and test certificates shall be furnished for approval. The Bidder shall indicate the details of the equipment available with him for carrying out the various tests as per relevant Standards. The bidder shall indicate the sources of all materials.

Note: The Meters used for conducting tests shall be calibrated periodically at reputed Government Accredited Test Laboratories and test certificates shall be available at works for verification by purchasers representative.

- SUBMISSION OF SAMPLE & DOCUMENTS

2 nos. sample meters (without CTs and box) having all the mentioned features, BCS with allied software and sample of seal etc. along with the Type Test Certificates, DLMS Certificate and with the test results and ISI Certificate, Tamper Logic, Display Parameters List is to be submitted to CGM/P&MM/TSSPDCL.

Offer will not be accepted without submission of sample and the Tender will not be opened. Any other accessories required for observing the performance & capabilities of the Meter are to be submitted along with offer.

- INSPECTION:

- The purchaser’s representative shall, at all times, be entitled to have access to the works and at all places of manufacture where equipment is offered, and manufactured and the representative shall have full facilities for unrestricted inspection of the bidder’s works, raw materials and process of manufacture and conducting necessary tests as detailed herein.

- The Bidder shall keep the purchaser informed in advance of the time of starting and of the progress of manufacture of the offered equipment in its various stages so that arrangements can be made for inspection.

- The supplier shall give 15 days advance intimation to enable the purchaser to depute his representative for witnessing acceptance and routine tests.

- No material shall be dispatched from its point of manufacture before it has been satisfactorily inspected and tested, unless the inspection is waived off, by the purchaser in writing.

- The acceptance of any quantity of material shall in no way relieve the Bidder of any of his responsibilities for meeting all requirements of the specification, and shall not prevent subsequent rejection if such material is later found to be defective.

- NOTE FOR FOREIGN BIDDERS:

The bidder shall indicate the name(s) of reputed inspection agencies and the inspection charges clearly for each lot. The inspection charges will be borne by the supplier. However the purchaser reserves the right to appoint at its cost any inspection agency to carry out the inspection.

17.0	QUALITY ASSURANCE PLAN:

The bidder shall invariably furnish the following information along with his bid, failing which his bid shall be liable for rejection. Information shall be separately given for individual type of material offered.

- The structure of organization.

- The duties and responsibilities assigned to staff ensuring quality of work.

- The system of purchasing, taking delivery and verification of materials.

- The system for ensuring quality of workmanship.

- The quality assurance arrangements shall conform to be relevant requirements of ISO 9001 or ISO 9002 as appropriate.

Statement giving list of important raw materials names of sub-suppliers for the raw materials, list of standards according to which the raw materials are tested. List of test normally carried out on raw materials in presence of Bidder’s representative, copies of test certificates.

- Information and copies of test certificates as in (vi) above in respect of bought out accessories.

- List of manufacturing facilities available.

- Level of automation achieved and list of areas where manual procession exists.

- List of areas in manufacturing process, where stage inspections are normally carried out for quality control and details of such tests and inspections.

- Lists of testing equipment available with the bidder for final testing of equipment specified and test plant limitation. If any, vis-a-vis the type, special acceptance and routine tests specified in the relevant standards. These limitations shall be very clearly brought out in schedule of deviations from specified test requirements.

The successful Contractor shall within 30 days of placement of order, submit following information to the purchaser.

  - List of raw materials as well as bought out accessories and the names of sub suppliers selected from those furnished along with offers.

  - Type test certificates of the raw materials and bought out accessories if required by the purchaser.

  - Quality assurance plan (QAP) with hold points for purchaser’s inspection. The quality assurance plan and purchasers hold points shall be discussed between the purchaser and Contractor before the QAP is finalized.

The Contractor shall submit the routine test certificates of bought out accessories and central excise asses for raw material at the time of routine testing if required by the purchaser and ensure that the quality assurance requirements of specification are followed by the sub-contractor.

The quality assurance programme shall give a description of the quality system and quality plans with the following details.

- Quality System:

  - The structure of the organisation.

  - The duties and responsibilities assigned to staff ensuring quality of work.

  - The system for purchasing, taking delivery and verification of materials.

  - The system for ensuring quality workmanship.

  - The system for control of documentation.

  - The system for the retention of records.

  - The arrangement for the contractor’s internal auditing.

A list of administration and work procedures required to achieve and verify contract’s quality requirements. These procedures shall be made readily available to the purchaser for inspection on request.

- Quality Plans:

  - An outline of the proposed work and programme sequence.

  - The structure of the contractors organisation for the contract.

  - The duties and responsibilities assigned to staff ensuring quality of work.

  - Hold and Notification points.

  - Submission of Engineering documents required by the Specification.

  - The inspection of materials and components on receipt.

  - Reference to the contractors work procedures appropriate to each activity.

  - Inspection during fabrication/Construction.

  - Final inspection and test.

- DOCUMENTATION:

- All drawings shall conform to International Standards Organisation (ISO) ‘A’ series of drawings sheet/India Standards Specifications IS :656. All drawings shall be in ink and suitable for micro filming. All dimensions and data shall be in S.I. Units.

- LIST OF DRAWINGS AND DOCUMENTS:

The bidder shall furnish the followings along with bid:

  - Two sets of drawings showing clearly the general arrangements, fitting details, electrical connections etc.

  - Technical leaflets (users manual giving operating instructions.)

  - Dimensional drawings of the box for each quoted item.

  - Dimensional drawings of the LT CTs where applicable for the quoted item.

- The manufacturing of the equipment shall be strictly in accordance with the approved drawings and no deviation shall be permitted without the written approval of the purchaser. All manufacturing and fabrication work in connection with the equipment prior to the approval of the drawing shall be at the supplier’s risk.

- Approval of drawings/work by purchaser shall not relieve the supplier of his responsibility and liability for ensuring correctness and correct interpretation of the drawings for meeting the requirements of the latest revision of application standards, rules and codes of practices. The equipment shall conform in all respects to high standards of engineering, design, workmanship and latest revisions of relevant standards at the time of ordering and purchaser shall have the power to reject any work or materials which, in his judgment is not in full accordance therewith.

- The successful Bidder shall, within 2 weeks of placement of order, submit three sets of final versions of all the drawings as stipulated in the purchase order for purchaser’s approval. The purchaser shall communicate his comments/ approval on the drawings to the supplier within two weeks. The supplier shall, if necessary, modify the drawings and resubmit three copies of the modified drawings for their approval. The supplier shall submit 3 prints with good quality of the approved drawings for purchaser’s use within one week.

- The successful bidder shall furnish a sample of box duly mounting the meter and CTs where applicable within two weeks of clear purchase order along with type tests certificates . Supplies shall commence only after approval of these.

- 18.7	Eight sets of operating manuals/technical leaflets shall be supplied to each consignee for the first instance of supply (The total no. of consignee is 5).

- One set of routine test certificates shall accompany each dispatch consignment.

- The acceptance test certificates in case pre-dispatch inspection is routine, test certificates in cases where inspection is waived shall be got approved by the purchaser.

- PACKING & FORWARDING:

- The equipment shall be packed in crates suitable for vertical/horizontal transport as the case may be and suitable to withstand handling during transport and outdoor storage during transit. The supplier shall be responsible for any damage to the equipment during transit, due to improper and inadequate packing. The easily damageable material shall be carefully packed and marked with the appropriate caution symbol. Wherever necessary, proper arrangement for lifting, such as lifting hooks etc., shall be provided. Any material found short inside the packing cases shall be supplied immediately by supplier without any extra cost.

- Each consignment shall be accompanied with a detailed packing list containing the following information.

  - Name of the consignee.

  - Details of consignment.

  - Destination.

  - Total weight of consignment.

  - Handling and packing instructions.

  - Bill of Material indicating contents of each package.

- The supplier shall ensure that the packing list and bill of materials are approved by the purchaser before dispatch.

- The packing shall be done as per the manufacturer’s standard practice. However, he should ensure the packing is such that, the material should not get damaged during transit by Rail/Road.

- The marking on each package shall be as per the relevant Standards and shall also contain PO reference, Name of the supplier, make, meter type and meter serial No.

QUANTITY AND DELIVERY REQUIREMENTS:

The quantity and delivery requirements indicated schedule.

- SUPERVISION SERVICES: NIL

The purchaser will arrange for unloading of the consignments.

- MANDATORY SPARES & TOOLS:

The bidder shall give the list of spares required for the equipment along with price list for them & shall keep a reasonable stock of the same during the warranty period. The bidder shall indicate the sources of spares like battery packs, interfacing cables in India and also mention the service agencies.

- TECHNICAL DEVIATIONS:

Any deviation in Technical Specification shall be specifically and clearly indicated in the enclosed Technical deviation format.

24.0	GUARANTEE:

  - The material should be guaranteed for satisfactory operation for a period of 5 years from the date of receipt of material at destination stores by the consignee in good condition. During the guarantee period if the meter while in its normal operation is found defective, it shall be replaced by the supplier with a new meter free of cost with in 15 days. If the meter is not replaced within 30 days of intimation the supplier should note that the guarantee period will be extended to that extent by the number of days delayed beyond 30 days. If the tenderer does not replace within 180 days the cost of the meter(s) will be recovered from the existing bills/ future bills/ Bank Guarantees available with TSSPDCL. It is in suppression of Clause 53.1  of section – I General and Financial Terms and conditions for supply of material in the booklet enclosed.

  - If the failure after erection and commissioning at site is more than 5% the TSSPDCL reserves the right to cancel the balance quantity of the order or take such suitable action as deemed fit. Minor defects during transit may be permitted to attend to in stores/ MRT Lab.

- GUARANTEED TECHNICAL PARTICULARS

The Bidder shall furnish the guaranteed Technical Particulars as per enclosed Annexure for L.T Electronic Trivector Meters, Annexure for LT CTs used in meters, & Annexure for Box used for meter and submit the same with the Tender.

- PERFORMANCE SECURITY:

The bidder has to give a guarantee of 10% of the contract value towards performance. If the Supplier fails to deliver any or all of the Materials/equipment or to perform the Services within the period(s) specified in the Contract, the Purchaser will, without prejudice to its other remedies under the Contract, deduct from the Contract Price, as liquidated damages, a sum equivalent to 0.5% per week on the undelivered portion subject to a maximum of 5% of the cost of the undelivered portion within scheduled time. Once the maximum is reached the Purchaser may consider termination of the contract.

- GENERAL:

  - Principle of operation of the meter, outlining the methods and stages of computation of various parameters starting from input voltage and current signals including the sampling rate if applicable shall be furnished by the bidder.

  - The bidder shall indicate the method adopted to transform the voltage and current to the desired low values with explanation on devices used such as CT, VT or Potential divider as to how they can be considered superior in maintaining ratio and phase angle for variation of influence quantities during its service period.

  - The bidder shall furnish details of memory used in the meter.

  - Details of testing facilities:

The manufacturer laboratory must be well equipped for testing of the meters. They must have computerized standard power source and standard equipment calibrated not later than a year (or as per standard practice). The details of testing facilities available for conducting (a) The routine tests and (b) Acceptance tests shall be furnished in a statement. Bids without these details will be treated as Non responsive.

- TECHNICAL SPECIFICATION FOR PP BOX TO HOUSE THE TRIVECTOR METER

- TECHNICAL DETAILS:

The box shall be weather proof made out of Sheet Moulding Compound (SMC) with flame retardant properties. It shall be capable of withstanding temperatures of boiling water for 5 minutes continuously without distortion or softening. The thickness of the box shall be not less than 3 mm on the load bearing side i.e. back side of the box and the other sides, door(s) and roof shall not be less than 2.5 mm. The boxes shall have its roof tapering down to both sides for easy flow of rain water.

- The dimension of the box shall be suitable for housing one number L.T Trivector meter. The box shall be of two separate compartments, the upper one to house the meter and the lower chamber to house the Four numbers ring type resin cast CTs (100/5A Ratio’s) and the neutral link. The inside dimensions of the upper box shall be such that there is a minimum clearance of 75mm on all sides and a clearance of 25mm at the front and back of the Trivector meter. The lower chamber shall be provided with 4 Nos. 30 mm dia holes with cable glands on either side for the incoming and outgoing cables. The base supports of the meter, and CTs shall be raised by above 10mm in the box for ease of wiring. The meter shall be mounted on a transparent polycarbonate sheet of minimum 6mm thickness. Frame and sealing arrangement shall be provided inside the box for fixing the meters. Meter mounting plate shall be such that the wires behind this plate are not at all accessible. A hole shall be provided for connecting the CT and PT leads to the meter through a suitable pipe. Suitable arrangements for mounting the box to a pole shall be provided.

- Both the chambers should have provision for sealing independently with

  - minimum of two seals each.

- A viewing window for noting the meter reading shall be provided on the door of the upper compartment.

- These boxes shall be suitable for outdoor installation. The construction shall be such that no rain water shall enter into the box. The boxes shall have a provision for sealing to make it fully tamper proof. The roof of the box shall be slanting in both sides. Soft rubber gaskets shall be provided wherever required for protection against entry of dust and water. It shall comply with IP-51. The boxes shall generally comply with the provisions of IS 5133 and IEC 695

- The dimensions of the box shall be with sufficient clearances to make connections without hindrance with the door(s) in open condition. The construction shall be such that no rain water shall enter into the box. Glands shall be provided for the box as per the requirement. 4No’s voltage clamps with copper lugs shall also be given along with the box.8No’s cable binding PVC clamps with screws for incoming and outgoing cables shall also be given with each box.

- Colour: Meter box shall be off white or admiralty grey.

THE CONTENTS OF THE BOX ARE AS FOLLOWS:

Viewing Window: Viewing Window made of a scratch and break resistant transparent polycarbonate/engineering plastic/toughened glass shall be provided on the door for meter reading without inconvenience. The minimum thickness of viewing window shall be 3mm. The viewing window should have a shade to protect the meter display from the direct sunlight. The window shall be ultra sonically welded with meter box from inside.

- There should not be any ingress of moisture through this window into the box.

- Internal hinges: A minimum of 2 Nos. internal hinges well protected against corrosion shall be provided for each door. The hinges of the door should be concealed and they shall be fixed to the flanges provided to the base and cover of the box in such a manner that the door opens by a minimum of 90 degrees.

- Handle: Suitable handle(s) or knob shall be provided for opening the box door(s).

- Earthing Bolt: 8mm dia GI bolt with 2nos washers for earthing all metal parts used for fixing the meter shall be provided.

- Fixing arrangement: While fixing the meter in the box, screws should not protrude outside. Suitable arrangements for mounting the box to a pole or wall shall be provided.

- Latch : Each door shall be provided with latch or a ‘U’ clamp to secure it with the base of the box.

- Sealing arrangement: The box shall have provision for minimum 2 nos. seals to each door to make it fully tamper proof.

- Printing: The Purchase Order No. & Month/Year of manufacturing shall be engraved with letters “TSSPDCL” on the top cover of the box. The name of the manufacture shall be engraved/metallic sheet duly riveted on the bottom half of the box. The words of guarantee period of ‘5’ Years’ must also be etched on the name plate in Red Colour. A blank sticker shall also be fixed on the meter for the use of field staff to indicate the service No., meter constant, CT ratio etc.

- The fixing arrangements shall not be complex and it shall be easily approachable for connections when the door(s) in open condition and is completely tamper proof once it is sealed.

- Wiring: The internal wiring inside the box shall be done neatly with 90 degrees bends with flexible PVC multi stranded copper wire of 2.5sq.mm (4 core or 10 core) maintaining the color code R-Y-B and with necessary looping (Grey/Black may be used for neutral).All potential wires shall pass through one duct and all currents wire shall pass through another duct from CT chamber to meter chamber.

- Dimensional drawing giving details of meter box shall be submitted.

29.0	SPECIFICATION FOR RESIN CAST RING TYPE CURRENT TRANSFORMER

  - The resin cast ring type LT Current Transformers conforming to IS-2705/1992 (Part I,II & III) or the latest version thereof, are of class 0.5S accuracy, 1VA burden for use in conjunction with -/5A Energy meters being supplied and are to be installed in a moulded box.

  - Ratings:  The Current Transformers shall be of the following details.

| Type |  | Resin cast ring type LT CTs (without bar) |  |
| --- | --- | --- | --- |
| Capacity |  | 100/5A |  |
| a) | Number of C.T’s | 4 No’s. |  |
| b) | Rated Voltage | 440V |  |
| c) | No. of Cores | One |  |
| d) Rated Burden |  | 1VA |  |
| e) Rated continuous Thermal |  | As per IS 2705/1992 or latest |  |
|  | Current temperature rise over | version thereof |  |
|  | ambient |  |  |
| f) | One minute withstand Power | 3Kv |  |
|  | Frequency Voltage |  |  |
| Class of Accuracy |  | 0.5S |  |
| Material |  |  |  |
| i) | Core | High grade non-ageing electrical |  |
|  |  | low loss core of superior CRGO |  |
| ii) | Conductor | silicon sheet steel |  |
|  |  | Super enameled copper wire |  |
| iii | Insulation | 2/1.22 mm |  |
| iv | Base | MS Hot dip galvanized |  |
| Secondary Termination |  | Terminals S1 & S2 shall be clearly marked |  |
|  |  | Transparent cover for CT secondary terminals |  |

### SECTION - VII

### SAMPLE FORMS

1.  BID FORM

Date.  .......

TO: (Name and Address of Purchaser)

Gentlemen and/or Ladies:

Having examined the Bidding documents, the receipt of which is hereby duly acknowledged, we, the undersigned, offer to supply and deliver.  ......................... (Description of Materials / equipment) in conformity with the said bidding documents in accordance with the prices quoted online and made part of this Bid.

We undertake, if our Bid is accepted, to deliver the Materials / equipment in accordance with the delivery schedule specified in the Schedule of Requirements.

If our Bid is accepted, we will obtain the guarantee of a bank in a sum equivalent to. 10% of the Contract Price for the due performance of the Contract, in the form prescribed by the Purchaser.

We agree to abide by this Bid up to ……………. (For the Bid Validity Period) specified in Clause and it will remain binding upon us and may be accepted at any time before the expiration of that period.

Until a formal contract is prepared and executed, this Bid, together with your written acceptance thereof and your notification of award, will constitute a binding Contract between us.

We understand that you are not bound to accept the lowest or any bid you may receive.

We certify / confirm that we comply with the eligibility requirements as per  clause  of the bidding documents.

Dated this.  ...........day of.  .............200

____________________________

____________________________

[Signature] 					[in the capacity of]

Duly authorized to sign Bid for and on behalf of _____________________________

2. (a) BID SECURITY FORM

Whereas.  .............. (hereinafter called "the Bidder") has submitted its Bid dated (date of submission of bid) for the supply of.  ....................(name and /or description of the Materials / equipment) (hereinafter called "the Bid").

KNOW ALL PEOPLE by these presents that WE.  .............(name of bank) having our registered office at.  ...........(address of bank)(hereinafter called "the Bank"), are bound unto.  ...............(name of Purchaser) (hereinafter called "the Purchaser") in the sum of                   for which payment well and truly to be made to the said Purchaser, the Bank binds itself, its successors, and assigns by these presents. Sealed with the Common Seal of the said Bank this          day of             200  .

THE CONDITIONS of this obligation are:

1.	If the Bidder

a) 	withdraws its Bid during the period of bid validity specified by the Bidder on the Bid Form; or

- does not accept the correction of errors in accordance with the Bid Specification, or

2.	If the Bidder, having been notified of the acceptance of its bid by the Purchaser during the period of bid validity;

(a)	fails or refuses to furnish the performance security, in accordance with the Bid Specification.

(b)	fails or refuses to execute the Contract Form if required; or

We undertake to pay the Purchaser up to the above amount upon receipt of its first written demand, without the Purchaser having to substantiate its demand, provided that in its demand the Purchaser will note that the amount claimed by it is due to it, owing to the occurrence of one or both of the two conditions, specifying the occurred condition or conditions.

This guarantee will remain in force up to and including forty five (45) days after …………….(Specification Date) the period of the bid validity, and any demand in respect thereof should reach the Bank not later than the above date.

.  ....................

(Signature of the Bank)

NOTE:	This will be executed on a Rs.100/- non-judicial stamp paper issued by a scheduled Bank.

2(b) PERFORMANCE SECURITY FORM

To:                        (Name of Purchaser)

WHEREAS………………………………………..(Name of Supplier)

(hereinafter called "the Supplier") has undertaken, in pursuance of Contract No.............dated.............200 to supply.  ................(Description of Materials / equipment and Services)

(hereinafter called "the Contract").

AND WHEREAS it has been stipulated by you in the said Contract that the Supplier will furnish you with a Bank Guarantee by a recognized Bank for the sum specified therein as security for compliance with the Supplier's performance obligations in accordance with the Contract.

AND WHEREAS we have agreed to give the Supplier a Guarantee:

THEREFORE WE hereby affirm that we are Guarantors and responsible to you, on behalf of the Supplier, up to a total of.  ............................ (Amount of the Guarantee in Words and Figures) and we undertake to pay you,  upon your first written demand declaring the Supplier to be in default under the Contract and without cavil or argument, any sum or sums within the limit of................ (Amount of Guarantee) as aforesaid, without your needing to prove or to show grounds or reasons for your demand or the sum specified therein.

This guarantee is valid until the.  ... day of.  ..... 200.

Signature and Seal of Guarantors

..........................................

Date.  .......................200.

..........................................

..........................................

Address:....................…...

..........................................

..........................................

NOTE:	This will be executed on a Rs.100/- non-judicial stamp paper by a scheduled Bank.

3. CONTRACT FORM

THIS AGREEMENT made the.  ....... day of.  ............ 200  Between.  ..............(Name of Purchaser) of the one part and.  ..........(Name of Supplier) of the other part:

WHEREAS   the Purchaser invited bids for certain Materials / equipment and ancillary services viz.,

.....................(Brief description of Materials / equipment and Services) and has accepted a bid by the Supplier for the supply of those Materials / equipment and services in the sum of.  .....................(Contract Price in Words and Figures)(hereinafter called "the Contract Price").

NOW THIS AGREEMENT WITNESSETH AS FOLLOWS:

1.	In this Agreement words and expressions will have the same meanings as are respectively assigned to them in the Conditions of Contract referred to.

2.	The following documents will be deemed to form and be read and construed as part of this Agreement, viz.:

(a)	the Bid Form and the Price Schedule submitted by the  Bidder;

(b)	the Schedule of Requirements;

(c)	the Technical Specifications;

(d)	the General Conditions of Contract;

(e)	the Purchaser's Notification of Award.

3.	In consideration of the payments to be made by the Purchaser to the Supplier as hereinafter mentioned, the Supplier hereby covenants with the Purchaser to provide the Materials / equipment and services and to remedy defects therein in conformity in all respects with the provisions of the Contract.

4.	The Purchaser hereby covenants to pay the Supplier in consideration of the provision of the Materials / equipment and services and the remedying of defects therein, the Contract Price or such other sum as may become payable under the provisions of the Contract at the times and in the manner prescribed by the Contract.

Brief particulars of the Materials / equipment and services which will be supplied/ provided by the Supplier are as under:

| Sl. No. | Brief Description of Materials / Equipment & services | Quantity to be supplied | Unit Price Rs. | Total Price Rs. | Delivery Terms |
| --- | --- | --- | --- | --- | --- |

TOTAL VALUE:	(Rupees 			     	 		only)

DELIVERY SCHEDULE:

IN WITNESS whereof the parties hereto have caused this Agreement to be executed on the day and year first above written.

Signed, Sealed and Delivered by the

said.  ..............................(for the Purchaser)

in the presence of.  ................

Signed, Sealed and Delivered by the

said.  ..............................(for the Supplier)

in the presence of.  ................

NOTE:	To be executed on a Rs.100/- Non-judicial stamp paper.

4.  PROFORMA FOR PERFORMANCE STATEMENT

Bid No.__________				Date of Opening________

Time _______ Hours

Name of the Firm__________________________________________

| Order placed by (full address of purchaser) | Order No. and Date | Description and quantity of ordered equipment | Date of Completion of Delivery |  |
| --- | --- | --- | --- | --- |
|  |  |  | As per Contract | Actual |

| Remarks indicating reasons for late delivery, if any | Has the equipment been satisfactorily functioning? (Attach a Certificate from the Purchaser) |
| --- | --- |

Signature of the Bidder _______________________

________________________

________________________

(FORMAT-A)

5. DETAILS TO BE FURNISHED BY THE MANUFACTURER

| 1. Specification No. | : |  |
| --- | --- | --- |
| 2. Name of the Material | : |  |
| 3. Quantity to be procured | : |  |
| 4. Last date and time for submission of Bid | : |  |
| 5. Date and time for opening of Bid | : |  |
| 6. State whether Bid guarantee is enclosed | : |  |
| 7. State whether the quotation in two parts has been submitted. | : |  |
| 8. State whether 20% minimum quantity is quoted | : |  |
| 9. Whether willing to furnish performance B.G. @ 10% if order is placed | : |  |
| 10. Whether month wise delivery schedule indicated | : |  |
| 11. Prices whether Firm | : |  |
| 12. Whether any other tax / duty payable. If so give details and the same is included / not included. | : |  |
| 13. State whether TSSPDCL(erstwhile TSSPDCL) terms of payment are accepted. | : |  |
| 14. Quantity offered for supply | : |  |
| 15. State whether 90 days validity offered | : |  |
| 16. Whether sample is enclosed (if specified) | : |  |
| 17. Whether the material / equipment offered conforms to the relevant TSSPDCL(erstwhile TSSPDCL) Specification | : |  |
| 18. Whether you have executed orders of the TSSPDCL(erstwhile TSSPDCL) previously for these items. (Please give details) | : |  |
| 19. Similar details in respect of supplies made to other utilities | : |  |
| 20. Whether Bid guarantee exemption letter enclosed, if exempted. | : |  |
| 21. Whether sales tax clearance certificate enclosed | : |  |
| 22. Whether Income-tax clearance certificate enclosed. | : |  |
| 23. Whether Warranty clause accepted | : |  |
| 24. Whether Penalty clause accepted | : |  |
| 25. Whether delivery schedule accepted | : |  |

6. SCHEDULE OF DEVIATION

# (i) TECHNICAL

| Sl. No. | Requirements / Equipment | Specification Clause No. | Deviations | Remarks |
| --- | --- | --- | --- | --- |

It is hereby conformed that except for deviations mentioned above, the offer conforms to all the other features specified in Technical Specification Section ____ of this Bid Document

Place :								Signature of the Bidder :

Date :								Name :

Business address  :

6. SCHEDULE OF DEVIATION

# (ii) COMMERCIAL

| Sl. No. | Requirements / Equipment | Specification Clause No. | Deviations | Remarks |
| --- | --- | --- | --- | --- |

It is hereby conformed that except for deviations mentioned above, the offer conforms to all the other features specified in Commercial Specification Section ____ of this Bid Document

Place :								Signature of the Bidder :

Date :								Name :

Business address:

r

Designation

Date:

7. DECLARATION FORM

Declaration to be given by the Company in regard to relation to promoters of Blacklisted / debarred companies by any power utilities.

I declare that, myself or any of the representatives of my company / firm do not have any relatives with promoters of blacklisted / debarred companies by any utilities.

It is certified that the information furnished above is true to the best of my knowledge and belief. It is hereby undertaken that in the event of the above information found to be false or incorrect at a later date, the TSSPDCL is entitled to terminate the contract/agreement entered into besides recovering damages as may be found necessary, with due notice.

Signature of authorized representative